## 3A HVAC BOQ
S.No | Category | Item Code | Description of Item | Lower Basement | Upper Basement | GF | 1F | 2F | 3F | 4F | 5F | 6F | Terrace | Total Quantity | Unit | Supply Rate (INR) | Installation Rate (INR) | Supply Amount (INR) | Installation Amount (INR) | Total Amount (INR) | REMARKS
|  |  |  | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | A=Q1 to Q10 |  | B | C | D=AxB | E=AxC | F=D+E
1 | HIGH SIDE EQUIPMENT | CHILLER | WATER COOLED VARIABLE SCREW CHILLERS WITH VFD : Supply, Installation, Testing, Commissioning of factory-assembled and tested, AHRI certified water cooled Variable Screw Chiller With unit mounted VFD complete Twin Screw Hermetic/ Open type type compressor complete with automatic capcity control safety switches, speed increasing gears forced fed lubrication system, microprocessor-based with MODBUS card, evaporator with factory insulation, water cooled condenser, controls, wiring, Electrical Starter panel with Weather-proof IP54 rated enclosure, Full charge of refrigerant, oil, Cushy foot/ spring mounting 2"deflection to meet acceptable vibration level , Grooved couplings for Cooler pipe connections, Internal refrigerant piping connections, suitable for STP water as inlet water for condenser, Refrigerant service valves (at Compressor inlet, outlet, Condenser outlet) Water flow switch for cooler & condenser and mounting frame, 2 year warranty from date of handing over, Equipment tagging and as per the technical specification furnished in this section. Refer technical specification for complete scope of work. | [14 empty] | 0 | 0 | 0
1.01 | HIGH SIDE EQUIPMENT | CHILLER | 1. Refrigeration Capacity: 300 TR actual Capacity at site condition. 2. Number of Passes: TWO 3. Minimum COP : 6.3 AHRI rating at full load condition & ikW/TR @ Design 0.61 kw/Tr NPLV 0.32 4. Refrigerant: R-134a 5. Chilled-Water Flow: 720 GPM - 45.42 LPS 6. Evaporator Entering-Water Temperature: 6.67 °C - 44 Deg F 7. Evaporator Leaving-Water Temperature: 12.2 °C - 54 Deg F 8. Evaporator Water-Pressure Drop: Not exceeding 60kPa 9. Evaporator Fouling Factor: 0.000102 (hr-sqft-F)/BTU 10. Condenser-Water Flow: 900 GPM - 56.7 LPS 11. Condenser Entering-Water Temperature: 28 Deg C - 82.4 Deg F 12. Condenser Leaving-Water Temperature: 33 Deg C - 91.4 Deg F 13. Condenser-Water Pressure Drop: Not exceeding 90kPa 14. Condenser Fouling Factor: 0.000250 (hr-sqft-F)/BTU 15. Electrical Characteristics: 415V ±10% AC, 3 p hase, 50 Hz, Squirrel cage induction motor | [10 empty] | 1 | Nos. |  | 156250 | 0 | 156250 | 156250
1.02 | HIGH SIDE EQUIPMENT | CHILLER | 1. Refrigeration Capacity: 350 TR actual Capacity at site condition. 2. Number of Passes: TWO 3. Minimum COP : 6.3 AHRI rating at full load condition & ikW/TR @ Design 0.61 kw/Tr NPLV 0.32 4. Refrigerant: R-134a 5. Chilled-Water Flow: 840 GPM - 45.42 LPS 6. Evaporator Entering-Water Temperature: 6.67 °C - 44 Deg F 7. Evaporator Leaving-Water Temperature: 12.2 °C - 54 Deg F 8. Evaporator Water-Pressure Drop: Not exceeding 60kPa 9. Evaporator Fouling Factor: 0.000102 (hr-sqft-F)/BTU 10. Condenser-Water Flow: 1050 GPM - 66.24 LPS 11. Condenser Entering-Water Temperature: 28 Deg C - 82.4 Deg F 12. Condenser Leaving-Water Temperature: 33 Deg C - 91.4 Deg F 13. Condenser-Water Pressure Drop: Not exceeding 90kPa 14. Condenser Fouling Factor: 0.000250 (hr-sqft-F)/BTU 15. Electrical Characteristics: 415V ±10% AC, 3 p hase, 50 Hz, Squirrel cage induction motor | [10 empty] | 1 | Nos. | 8497684 | 156250 | 8497684 | 156250 | 8653934
1.03 | HIGH SIDE EQUIPMENT | AUTOMATIC TUBE CLEAINNG SYSTEM | Supply, Installation, Testing & commissioning of automatic tube cleaning systemfor water cooled chillers comprising of the following complete as per specification and as required with following components.The cost shall inclusive of balls strainer - 200 mm type inline Y/T shape, collector, local control panel, booster pump, control valve for injection & collection, motorized control valves, manual check valves (complete set for 4 ball traps & collectors), all skid mounted ready for installation. | [10 empty] | 3 | Nos. | 1166000 | 93750 | 3498000 | 281250 | 3779250
1.04 | HIGH SIDE EQUIPMENT | INSTALLATION OF EXISTING CHILLER | Installation, Testing, commisioning of existing 350 TR chiller and required necessry maintenance to startup the chiller. The chiller is available at site. Necessary assesment to be done by Contractor for the existing chiller machine. Make: Climaveneta WDH - 32 -480 Year of installation : 2010 | [10 empty] | 1 | Nos. | 0 | 156250 | 0 | 156250 | 156250
1.05 | HIGH SIDE EQUIPMENT | FACTORY TEST | Please quote the price of carrying out factory testing of one number of chiller as per procedure laid down by AHRI at 100%, 75%, 50% ,25% loading at constant CDW entry of 28 deg C. Please do not include clients travel expenditure. | [10 empty] | 1 | LOT | 502700 | 43750 | 502700 | 43750 | 546450 | We have considered factory test for one chiller
2 | HIGH SIDE EQUIPMENT | COOLING TOWER | LOW APPROACH INDUCED DRAFT COUNTERFLOW COOLING TOWER: Supply, Installation, Testing and Commissioning of Induced draft Twin/ Multi Fan FRP Cooling tower with PVC fillings with integral louvers and drift eliminators open pan gravity flow distribution system suitable for water distribution complete with hot FRP water basin header and branch system fitted with spray nozzles , statically and dynamically balanced axial flow type fan-direct driven/ Belt driven or driven through special beveled reduction gear box with TEFC induction motor with IP-55 protection,IE-3, Suitable for VFD application for running round the clock , suction screen made of SS 304 L, make up and quick fill, hardware of SS 304 L, fill arrangement, equalizer line, overflow and drain connections and suitable inspection HDG ladder, access arrangement for cooling tower interior, anti vibration mountings etc. complete as per specifications and as required. Kindly note that selection should be such that CTI 201 ceritfied model is being selected to meet the parameters and complies to CTI ATC 105 test requirements. | [12 empty] | 0 | 0
2.01 | HIGH SIDE EQUIPMENT | COOLING TOWER | Heat Rejection Capacity: 17,46,000 Kcal/Hr Ambient Wet Bulb Temperature: 26.3 °C RH: 75% Cooling Tower Entering Water Temperature: 33°C Cooling Tower Leaving Water Temperature: 28°C Cooling tower Range : 5°C Cooling Tower Approach : Minimum 1.7°C Drift Loss : <.005% Evaporation Loss : < .75% | Q10: 2 | 2 | EACH | 1878188 | 163013 | 3756376 | 326026 | 4082402 | We have not considerd CTI series due to low approach ,as mentioned in the BOQ
3 | HIGH SIDE EQUIPMENT | VARIABLE PRIMARY CHILLED WATER PUMPS | VARIABLE PRIMARY CHILLED WATER HORIZONTAL END SUCTION PUMPS WITH VFD : Supply,Installation, testing & commissioning of following capacity factory assembled and tested, End suction centrifugal pump designed for installation with pump and motor shafts mounted horizontally with factory fabricated base frame, Completely (Pump & its components) insulated with Flexible Closed-cell nitrile rubber insulating material and covered with 0.8-mm thick aluminium cladding material. The aluminium cladding shall have suitably placed screws to remove the cladding for pump servicing purpose. Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F). The motor shall be suitable for variable speed operation, The pump efficiency shall be IE3. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
3.01 | HIGH SIDE EQUIPMENT | VARIABLE PRIMARY CHILLED WATER PUMPS | Flow Rate 258 m3/hr, 35 m Head | [10 empty] | QRO | EACH | 519214 | 25000 | 0 | 0 | 0
4 | HIGH SIDE EQUIPMENT | VARIABLE PRIMARY CHILLED WATER PUMPS | VARIABLE CHILLED WATER PUMPS WITH VFD : Supply,Installation, testing & commissioning of following capacity factory assembled and tested, END SUCTION centrifugal, ; designed for installation with pump and motor shafts mounted vertically with factory fabricated base frame, IP-55 rated inbuilt motor mounted VFD with logic controller, Completely (Pump & its components) insulated with Flexible Closed-cell nitrile rubber insulating material and covered with 0.8-mm thick aluminium cladding material. The aluminium cladding shall have suitably placed screws to remove the cladding for pump servicing purpose. Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F). The motor shall be suitable for variable speed operation,The pump and motor should have cushion for flow and head adjustment of atleast 15%. The pump motor efficiency shall be IE3. The pump should be installed with inertia base with enclosed spring minimum 1" deflection. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
4.01 | HIGH SIDE EQUIPMENT | VARIABLE PRIMARY CHILLED WATER PUMPS | Flow Rate 258 m3/hr, 15 m Head | [10 empty] | QRO | EACH | 519214 | 25000 | 0 | 0 | 0
5 | HIGH SIDE EQUIPMENT | PRIMARY CHILLED WATER PUMPS | PRIMARY CHILLED WATER PUMPS - END SUCTION : Supply,Installation, testing & commissioning of following capacity factory assembled and tested, End-suction centrifugal, ; designed for installation with pump and motor shafts mounted vertically with factory fabricated base frame, coupling guard, Completely (Pump & its components) insulated with Flexible Closed-cell nitrile rubber insulating material and covered with 0.8-mm thick aluminium cladding material. The aluminium cladding shall have suitably placed screws to remove the cladding for pump servicing purpose. Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F).The pump and motor should have cushion for flow and head adjustment of atleast 15%. The motor shall be rated for variable speed operation, The pump motor efficiency shall be IE3. The pump should be installed with inertia based with enclosed spring minimum 1" deflection. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
5.01 | HIGH SIDE EQUIPMENT | PRIMARY CHILLED WATER PUMPS | Flow rate 520 GPM 32.8 LPS 15 Mtr Head | Q10: 4 | 4 | EACH | 187296 | 25000 | 749184 | 100000 | 849184
6 | HIGH SIDE EQUIPMENT | SECONDARY PUMPS | SECONDARY CHILLED WATER PUMPS - END SUCTION : Supply,Installation, testing & commissioning of following capacity factory assembled and tested, centrifugal, end-suction pump coupling guard, mounted horizontally with factory fabricated base frame, Completely (Pump & its components) insulated with Flexible Closed-cell nitrile rubber insulating material and covered with 0.8-mm thick aluminium cladding material. The aluminium cladding shall have suitably placed screws to remove the cladding for pump servicing purpose. Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F).The pump and motor should have cushion for flow and head adjustment of atleast 15%. The motor shall be suitable for variable speed operation. The pump should be installed with inertia based with enclosed spring minimum 1" deflection. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
6.01 | HIGH SIDE EQUIPMENT | SECONDARY PUMPS | Flow 1080 GPM 68.1 LPS 18 Mtr Head - Shaft - 1 | Q10: 2 | 2 | EACH | 339093 | 25000 | 678186 | 50000 | 728186
6.02 | HIGH SIDE EQUIPMENT | SECONDARY PUMPS | Flow rate 300 GPM 18.9 LPS 20 Mtr Head - Shaft - 2 | Q10: 2 | 2 | EACH | 186965 | 25000 | 373930 | 50000 | 423930
6.03 | HIGH SIDE EQUIPMENT | SECONDARY PUMPS | Flow rate 786 GPM 49.6 LPS 25 Mtr Head - Shaft - 3 | Q10: 2 | 2 | EACH | 338321 | 25000 |  | 50000 | 50000
6.04 | HIGH SIDE EQUIPMENT | SECONDARY PUMPS | Flow rate 285 GPM 18 LPS 12 Mtr Head - Only OT | Q10: 2 | 2 | EACH | 152315 | 25000 | 304630 | 50000 | 354630
7 | HIGH SIDE EQUIPMENT | CONDENSER CHILLED WATER PUMPS | CONDENSER WATER HORIZONTAL END SUCTION PUMPS : Supply,Installation, testing & commissioning of following capacity factory assembled and tested, End suction centrifugal pump designed for installation with pump and motor shafts mounted horizontally with factory fabricated base frame,coupling guard, Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F). The motor shall be suitable for variable speed operation, The pump efficiency shall be IE3.The pump and motor should have cushion for flow and head adjustment of atleast 15%. The pump should be installed with inertia base with enclosed spring minimum 1" deflection. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
7.01 | HIGH SIDE EQUIPMENT | CONDENSER CHILLED WATER PUMPS | Flow rate758.8 GPM 47.8 LPS 22 Mtr Head | Q10: 4 | 4 | EACH | 280226 | 25000 | 1120904 | 100000 | 1220904
8 | HIGH SIDE EQUIPMENT | CONDENSER CHILLED WATER PUMPS | CONDENSED WATER PUMPS : (VERTICAL INLINE PUMP) Supply,Installation, testing & commissioning of following capacity factory assembled and tested, INLINE centrifugal, ; designed for installation with pump and motor shafts mounted vertically with factory fabricated base frame, Completely (Pump & its components) insulated with Flexible Closed-cell nitrile rubber insulating material and covered with 0.8-mm thick aluminium cladding material. The aluminium cladding shall have suitably placed screws to remove the cladding for pump servicing purpose. Provide necessary tags as per Specification. Rate pump for 1600kPa (232) PSIG) minimum working pressure and a continuous water temperature of 45 Deg C (113+Deg F). The motor shall be suitable for variable speed operation, The pump motor efficiency shall be IE3. Please refer Tender Specifications for further details. | [12 empty] | 0 | 0
8.01 | HIGH SIDE EQUIPMENT | CONDENSER CHILLED WATER PUMPS | Flow Rate 290 m3/hr, 20m Head | Q10: QRO | QRO | EACH | 408804 | 25000 | 0 | 0 | 0
9 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (50-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Filtration section AHU filter section washable type of "G4" Pre-filter with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus.Noise level of the fan to be selected below 65dBA. The quoted price should be included with neoprene rubber isolators for AHU support | [12 empty] | 0 | 0
9.01 | AIR HANDLING EQUIPMENT | AHU | 3TR,3800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 179573 | 8750 | 179573 | 8750 | 188323 | bar: Q7
9.02 | AIR HANDLING EQUIPMENT | AHU | 1.5TR,1600 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 143003 | 4375 | 0 | 0 | 0
9.03 | AIR HANDLING EQUIPMENT | AHU | 8.0TR,7500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 251505 | 15625 | 251505 | 15625 | 267130 | bar: Q6
9.04 | AIR HANDLING EQUIPMENT | AHU | 6.0TR,5000 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 219506 | 15625 | 219506 | 15625 | 235131 | bar: Q9
9.05 | AIR HANDLING EQUIPMENT | AHU | 4TR,4800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 217954 | 15625 | 217954 | 15625 | 233579 | bar: Q8
9.06 | AIR HANDLING EQUIPMENT | AHU | 14TR,14300 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 362768 | 18750 | 362768 | 18750 | 381518 | bar: Q5
9.07 | AIR HANDLING EQUIPMENT | AHU | 10TR,7100 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 248486 | 15625 | 248486 | 15625 | 264111 | bar: Q3
10 | AIR HANDLING EQUIPMENT | AHU | Ceiling Suspended Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Side Discharge, ceiling suspended air-handling units. AHU Casing Section Double Skin, thermal break profile (25-mm thick CFC Free PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Filtration section, the casing should be desgined such that breakout noise should not exceed mor than 50 Dba and measure to achieve the same to be taken. AHU filter section washable type of "G4" Pre-filter with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below55 dBA. The quoted price should be included with rubber isolators for AHU support | [12 empty] | 0 | 0
10.01 | AIR HANDLING EQUIPMENT | AHU | 1TR,550 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 142485 | 4375 | 142485 | 4375 | 146860 | bar: Q1
10.02 | AIR HANDLING EQUIPMENT | AHU | 2.0TR,2300 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 150075 | 6250 | 150075 | 6250 | 156325 | bar: Q4
10.03 | AIR HANDLING EQUIPMENT | AHU | 2TR,1300 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 142485 | 4375 | 0 | 0 | 0
10.04 | AIR HANDLING EQUIPMENT | AHU | 2TR,1700 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 145418 |  | 145418 | 0 | 145418 | bar: Q1
10.05 | AIR HANDLING EQUIPMENT | AHU | 2TR,2000 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 147574 | 6250 | 147574 | 6250 | 153824 | bar: Q6
10.06 | AIR HANDLING EQUIPMENT | AHU | 3TR,2800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 157320 | 6250 | 157320 | 6250 | 163570 | bar: Q4
10.07 | AIR HANDLING EQUIPMENT | AHU | 2TR,2400 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 150938 | 6250 | 0 | 0 | 0
10.08 | AIR HANDLING EQUIPMENT | AHU | 2TR,2700 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 153439 | 6250 | 153439 | 6250 | 159689 | bar: Q7
10.09 | AIR HANDLING EQUIPMENT | AHU | 2.5TR,2200 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 149213 | 6250 | 0 | 0 | 0
10.1 | AIR HANDLING EQUIPMENT | AHU | 3TR,1600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 144555 | 4375 | 144555 | 4375 | 148930 | bar: Q8
10.11 | AIR HANDLING EQUIPMENT | AHU | 3TR,2500 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 151800 | 6250 | 0 | 0 | 0
10.12 | AIR HANDLING EQUIPMENT | AHU | 3TR,2600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 152576 | 6250 | 152576 | 6250 | 158826 | bar: Q8
10.13 | AIR HANDLING EQUIPMENT | AHU | 4TR,3300 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 161546 | 9375 | 161546 | 9375 | 170921 | bar: Q1
10.14 | AIR HANDLING EQUIPMENT | AHU | 4TR,3400 CMH, 250 Pa External Static pressure | [10 empty] | 2 | EACH | 169395 | 9375 | 338790 | 18750 | 357540 | bar: Q1; Q3
10.15 | AIR HANDLING EQUIPMENT | AHU | 5TR,4500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 247451 | 9375 | 247451 | 9375 | 256826 | bar: Q9
10.16 | AIR HANDLING EQUIPMENT | AHU | 3TR,3400 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 169481 | 9375 | 0 | 0 | 0
10.17 | AIR HANDLING EQUIPMENT | AHU | 3TR,4250 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 178106 | 9375 | 0 | 0 | 0
10.18 | AIR HANDLING EQUIPMENT | AHU | 4TR,3700 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 173794 | 9375 | 173794 | 9375 | 183169 | bar: Q1
10.19 | AIR HANDLING EQUIPMENT | AHU | 4TR,4200 CMH, 250 Pa External Static pressure | [10 empty] | 2 | EACH | 177675 | 9375 | 355350 | 18750 | 374100 | bar: Q1; Q3
10.2 | AIR HANDLING EQUIPMENT | AHU | 4TR,4500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 247451 | 9375 | 247451 | 9375 | 256826 | bar: Q3
10.21 | AIR HANDLING EQUIPMENT | AHU | 6TR,6400 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 269963 | 12500 | 269963 | 12500 | 282463 | bar: Q4
10.22 | AIR HANDLING EQUIPMENT | AHU | 6TR,7400 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 287816 | 12500 | 287816 | 12500 | 300316 | bar: Q3
10.23 | AIR HANDLING EQUIPMENT | AHU | 7TR,5200 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 257715 | 9375 | 257715 | 9375 | 267090 | bar: Q10
10.24 | AIR HANDLING EQUIPMENT | AHU | 5TR,5900 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 294533 | 9375 | 294533 | 9375 | 303908 | bar: Q4
10.25 | AIR HANDLING EQUIPMENT | AHU | 5TR,5000 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 251246 | 9375 | 251246 | 9375 | 260621 | bar: Q1
10.26 | AIR HANDLING EQUIPMENT | AHU | 5TR,4700 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 249263 | 9375 | 0 | 0 | 0
10.27 | AIR HANDLING EQUIPMENT | AHU | 5TR,2800 CMH, 250 Pa External Static pressure | Q2: 2 | 2 | EACH | 157320 | 6250 | 314640 | 12500 | 327140
10.28 | AIR HANDLING EQUIPMENT | AHU | 5TR,3300 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 161546 | 9375 | 161546 | 9375 | 170921 | bar: Q3
10.29 | AIR HANDLING EQUIPMENT | AHU | 13TR,10600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 320850 | 15625 | 320850 | 15625 | 336475 | bar: Q10
10.3 | AIR HANDLING EQUIPMENT | AHU | 7TR,9400 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 307481 | 15625 | 307481 | 15625 | 323106 | bar: Q4
10.31 | AIR HANDLING EQUIPMENT | AHU | 6TR,4200 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 177675 | 9375 | 177675 | 9375 | 187050 | bar: Q4
10.32 | AIR HANDLING EQUIPMENT | AHU | 16TR,15500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 339653 | 18750 | 339653 | 18750 | 358403 | bar: Q10
10.33 | AIR HANDLING EQUIPMENT | AHU | 14TR,14600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 354660 | 18750 | 354660 | 18750 | 373410 | bar: Q10
10.34 | AIR HANDLING EQUIPMENT | AHU | 18TR,11700 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 337841 | 15625 | 337841 | 15625 | 353466 | bar: Q3
10.35 | AIR HANDLING EQUIPMENT | AHU | 12TR,11600 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 337238 | 15625 | 0 | 0 | 0
11 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (25-mm thick CFC Free PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Filtration section AHU filter section washable type of "G4" Pre-filter with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Medium Filtration section AHU filter section of "F5" Fine-filter section with MERV 10 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 60%.. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected belown 65dBA.The quoted price should be included with rubber isolators for AHU support. Fans for unit of 44300 and 50300 CHM should be of EC+ technology | [12 empty] | 0 | 0
11.01 | AIR HANDLING EQUIPMENT | AHU | 42 TR, 44300 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 2290291 | 37500 | 2290291 | 37500 | 2327791 | bar: Q3
11.02 | AIR HANDLING EQUIPMENT | AHU | 41.0TR,33000 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 966330 | 31250 | 966330 | 31250 | 997580 | bar: Q4
11.03 | AIR HANDLING EQUIPMENT | AHU | 62TR,50700 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 2418854 | 43750 | 2418854 | 43750 | 2462604 | bar: Q4
11.04 | AIR HANDLING EQUIPMENT | AHU | 57TR,50700 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 2418854 | 43750 | 2418854 | 43750 | 2462604 | bar: Q5
11.05 | AIR HANDLING EQUIPMENT | AHU | 14TR,11100 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 365670 | 15625 | 365670 | 15625 | 381295 | bar: Q6
12 | AIR HANDLING EQUIPMENT | AHU | Ceiling Suspended Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Ceiling suspended air-handling units. AHU Casing Section Double Skin, thermal break profile (25-mm thick CFC Free PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Filtration section. the casing should be desgined such that breakout noise should not exceed mor than 50 Dba and measure to achieve the same to be taken. AHU filter section washable type of "G4" Pre-filter with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Medium Filtration section AHU filter section of "F5" Fine-filter section with MERV 10 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 60%.. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 55dBA @1 Mtr.The quoted price should be included with rubber isolators for AHU support. | [12 empty] | 0 | 0
12.01 | AIR HANDLING EQUIPMENT | AHU | 9.0TR,8400 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 348536 | 12500 | 348536 | 12500 | 361036 | bar: Q3
12.02 | AIR HANDLING EQUIPMENT | AHU | 11.0TR,7600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 341205 | 12500 | 341205 | 12500 | 353705 | bar: Q3
12.03 | AIR HANDLING EQUIPMENT | AHU | 16.0TR,12000 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 408998 | 15625 | 408998 | 15625 | 424623 | bar: Q9
12.04 | AIR HANDLING EQUIPMENT | AHU | 5TR,5200 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 297821 | 9375 | 297821 | 9375 | 307196 | bar: Q8
12.05 | AIR HANDLING EQUIPMENT | AHU | 6TR,6500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 312139 | 9375 | 312139 | 9375 | 321514 | bar: Q7
13 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (50-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section (MERV 8) with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 65dBA.The quoted price should be included with the PCC pedestal and rubber isolators for AHU support | [12 empty] | 0 | 0
13.01 | AIR HANDLING EQUIPMENT | AHU | 9.0TR,16000 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 579341 | 18750 | 579341 | 18750 | 598091 | bar: Q9
13.02 | AIR HANDLING EQUIPMENT | AHU | 4.0TR,3800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 254351 | 9375 | 254351 | 9375 | 263726 | bar: Q1
13.03 | AIR HANDLING EQUIPMENT | AHU | 3.0TR,3100 CMH, 350 Pa External Static pressure | [10 empty] | QRO | EACH | 205189 | 9375 | 0 | 0 | 0
13.04 | AIR HANDLING EQUIPMENT | AHU | 5.0TR,6300 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 291180 | 12500 | 291180 | 12500 | 303680 | bar: Q6
13.05 | AIR HANDLING EQUIPMENT | AHU | 4.0TR,4500 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 260475 | 9375 | 260475 | 9375 | 269850 | bar: Q6
13.06 | AIR HANDLING EQUIPMENT | AHU | 2.0TR,2600 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 189491 | 6250 | 189491 | 6250 | 195741 | bar: Q6
13.07 | AIR HANDLING EQUIPMENT | AHU | 7.0TR,5100 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 265391 | 9375 | 265391 | 9375 | 274766 | bar: Q7
13.08 | AIR HANDLING EQUIPMENT | AHU | 2.0TR,2800 CMH, 350 Pa External Static pressure | [10 empty] | QRO | EACH | 195788 | 6250 | 0 | 0 | 0
13.09 | AIR HANDLING EQUIPMENT | AHU | 7.0TR,6000 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 288593 | 12500 | 288593 | 12500 | 301093 | bar: Q9
13.1 | AIR HANDLING EQUIPMENT | AHU | 11TR,9300 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 324731 | 15625 | 324731 | 15625 | 340356 | bar: Q9
13.11 | AIR HANDLING EQUIPMENT | AHU | 7TR,6900 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 305325 | 12500 | 305325 | 12500 | 317825 | bar: Q9
14 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (50-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section (MERV 8) with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s dual flow (CHW+DX).The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation.The chilled water coil should be designed suitable of 4.5 & 5.5 TR and DX Coil designed suitable of 4.5 & 5.5 TR Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 65dBA.The quoted price should be included with the PCC pedestal and rubber isolators for AHU support | [12 empty] | 0 | 0
14.01 | AIR HANDLING EQUIPMENT | AHU | 9.0TR,16000 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 732263 | 18750 | 732263 | 18750 | 751013 | bar: Q9
14.02 | AIR HANDLING EQUIPMENT | AHU | 11TR,9300 CMH, 350 Pa External Static pressure | [10 empty] | 1 | EACH | 420383 | 15625 | 420383 | 15625 | 436008 | bar: Q9
15 | AIR HANDLING EQUIPMENT | AHU | Ceiling Suspended Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Side Discharge, Ceiling suspended air-handling units. AHU Casing Section Double Skin, thermal break profile (25-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section (MERV 8) with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 55dBA.The quoted price should be included with Spring isolators for AHU support | [12 empty] | 0 | 0
15.01 | AIR HANDLING EQUIPMENT | AHU | 2.0TR,2500 CMH, 350 Pa External Static pressure | Q9: 2 | 2 | EACH | 180004 | 6250 | 360008 | 12500 | 372508
15.02 | AIR HANDLING EQUIPMENT | AHU | 1.0TR,800 CMH, 150 Pa External Static pressure | [10 empty] | 1 | EACH | 165945 | 4375 | 165945 | 4375 | 170320 | bar: Q7
15.03 | AIR HANDLING EQUIPMENT | AHU | 3.0TR,4100 CMH, 150 Pa External Static pressure | [10 empty] | 1 | EACH | 272809 | 9375 | 272809 | 9375 | 282184 | bar: Q9
15.04 | AIR HANDLING EQUIPMENT | AHU | 3.0TR,4000 CMH, 150 Pa External Static pressure | Q9: 6 | 6 | EACH | 210105 | 9375 | 1260630 | 56250 | 1316880
15.05 | AIR HANDLING EQUIPMENT | AHU | 5TR,3800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 270308 | 9375 | 270308 | 9375 | 279683 | bar: Q5
15.06 | AIR HANDLING EQUIPMENT | AHU | 8TR,8000 CMH, 250 Pa External Static pressure | [10 empty] | QRO | EACH | 345949 | 15625 | 0 | 0 | 0
15.07 | AIR HANDLING EQUIPMENT | AHU | 7TR,7800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 344138 | 12500 | 344138 | 12500 | 356638 | bar: Q7
15.08 | AIR HANDLING EQUIPMENT | AHU | 5TR,6200 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 310155 | 12500 | 310155 | 12500 | 322655 | bar: Q1
16 | AIR HANDLING EQUIPMENT | AHU | Ceiling Suspended Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Side Discharge, Ceiling suspended air-handling units. AHU Casing Section Double Skin, thermal break profile (25-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section (MERV 8) with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. Coil Section The cooling coil should be minimum 6 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s dual flow (CHW+DX) .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation.The chilled water coil should be designed suitable of 4TR and DX Coil designed suitable of 4 TR. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 55dBA.The quoted price should be included with spring isolators for AHU support | [12 empty] | 0 | 0
16.01 | AIR HANDLING EQUIPMENT | AHU | 8TR,8000 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 507668 | 15625 | 507668 | 15625 | 523293 | bar: Q6
16.02 | AIR HANDLING EQUIPMENT | AHU | 7TR,7800 CMH, 250 Pa External Static pressure | [10 empty] | 1 | EACH | 441428 | 15625 | 441428 | 15625 | 457053 | bar: Q6
17 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (50-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section with MERV 8 with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. Coil Section The cooling coil should be minimum 8 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s with dual flow (CHW+DX) .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. The chilled water coil should be designed suitable of 9TR and DX Coil designed suitable of 9 TR. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 65dBA. The quoted price should be included with the PCC pedestal and rubber isolators for AHU support | [12 empty] | 0 | 0
17.01 | AIR HANDLING EQUIPMENT | AHU | 18TR,24200 CMH, 850 Pa External Static pressure | Q9: 2 | 2 | EACH | 1117321 | 31250 | 2234642 | 62500 | 2297142
18 | AIR HANDLING EQUIPMENT | AHU | Floor Mounted Air Handling Units (Horizontal Type) : Design, Supply, Installation, Testing and commissioning of factory made horizontal, Top Discharge, Floor mounted air-handling units. AHU Casing Section Double Skin, thermal break profile (50-mm thick PUF panels of 40kg/m3 with 0.6-mm thick inner GI & 0.8-mm outer skin pre-coated GI). The AHU casing frame structure shall be made of minimum 40mm GSS with Aluminium frame work with thermal break profiles. Add Return air plenum with provision for return air and fresh air duct with volume control damper connection. Pre Filtration section AHU filter section washable type of "G4" Pre-filter section with MERV 8 with filter frame. Pressure test ports shall be provided before and after each filter section.Please include the cost of one set of Pre-commissioning filter for building flush out before occupation to be considered for each AHU's. Fine Filtration section AHU filter section of "F7" Fine-filter section with MERV 13 with filter frame. Pressure test ports shall be provided before and after each filter section.The filter to be selected low pressure drop with better efficiency min 90%. These AHUs should account for HEP Filter at terminal Coil Section The cooling coil should be minimum 8 row coil made of 12.5mm diameter copper tube with aluminium fins 12 fins per inch and the face velocity of cooling coil shall not exceed 2.5m/s .The coil shall be made of Copper header and MS adopter with grooved ends.The selected cooling coil should be AHRI Certified and as per the provided AHU schedule. There should be minimum space of 50mm between cooling coil and filter section.The coil section shall be provided with 1.2mm thick SS304 drain pan with 13mm thick closed cell nitrile rubber insulation. Fan Section Mutiple module of Direct driven Plug type fans with EC motor, necessary mounting frame, Vibration isolators, 2mm thick GI base frame, Aluminium structural frame work, Marine light, Access door and Access door limit switch, View port for fan section, accessories and as per technical specifications. Selected EC fan should be BMS compatible with Modbus. Noise level of the fan to be selected below 65dBA.The quoted price should be included with rubber isolators for AHU support | [12 empty] | 0 | 0
18.01 | AIR HANDLING EQUIPMENT | AHU | 6TR,11600 CMH, 850 Pa External Static pressure | Q9: 8 | 8 | EACH | 495000 | 15625 | 3960000 | 125000 | 4085000
18.02 | AIR HANDLING EQUIPMENT | AHU | 7TR,7600 CMH, 850 Pa External Static pressure | [10 empty] | 1 | EACH | 345870 | 12500 | 345870 | 12500 | 358370 | bar: Q7
18.03 | AIR HANDLING EQUIPMENT | AHU | 6TR,6100 CMH, 850 Pa External Static pressure | [10 empty] | 1 | EACH | 318960 | 12500 | 318960 | 12500 | 331460 | bar: Q7
18.04 | AIR HANDLING EQUIPMENT | AHU | 5TR,5500 CMH, 850 Pa External Static pressure | [10 empty] | 1 | EACH | 312030 | 9375 | 312030 | 9375 | 321405 | bar: Q5
19 | TREATED FRESH AIR EQUIPMENT | IEC | Treated Fresh Air Pre Cooling Unit - Single-Stage - Indirect Evaporative Cooling (IEC)- : Design, Supply, Installation, Testing, and commissioning of factory-made, Floor mounted Double Skin, (44-mm thick CFC free PUF panels with 0.8-mm thick inner GI plain &1-mm thick outer GI precoated skin) horizontal air-handling units, Pre-filter & Fine FIlter section MERV 8 & MERV 13 with filter frame within plenum (min. 500 mm length), blow through type fan arrangement with EC+ fan rated for both supply airflow rate & scavenging airflow, drive motor (Efficiency class IE5), a sensible heat exchanger on with minimum sensible cooling efficiency of 80% for peak summer design conditions, distribution baffles, secondary air outlet plenum, inbuilt SS recirculation pump, inbuilt main sump fabricated of 1.2 mm thick SS 304, provisions to receive water supply with isolation valves and float valves, necessary mounting frame, Vibration isolators, 1.6 mm thick GI base frame, Aluminum structural framework, Fire retardant UV resistant flexible connection, Access door, outdoor mountable electrical starter panel with VFD which shall have required circuit breakers to operate fans & circulation pump through external BMS and accessories including equipment tagging and as per technical specifications furnished in this section. Please provide necessary blank plates to isolate the pipe header and spray arrangements.The no. of fans inside the AHU shall be limited to two. If the AHU has got two fans, two additional sub-breakers have to be considered in the electrical panel’s cost. | [12 empty] | 0 | 0
19.01 | TREATED FRESH AIR EQUIPMENT | IEC | 30000 CMH, 250 Pa External Static pressure | Q10: 2 | 2 | EACH | 2235207 | 56250 | 4470414 | 112500 | 4582914
19.02 | TREATED FRESH AIR EQUIPMENT | IEC | 31500 CMH, 250 Pa External Static pressure | Q10: 2 | 2 | EACH | 2315225 | 56250 | 4630450 | 112500 | 4742950
19.03 | TREATED FRESH AIR EQUIPMENT | IEC | 7000 CMH, 100 Pa External Static pressure | [10 empty] | QRO | EACH | 126500 | 18750 | 0 | 0 | 0
20 | TREATED FRESH AIR PANEL | IEC PANEL | Electrical Starter Panel The vendor shall include the price of Supply, Installation, Testing & Commissioning of Electrical Control Panel made of 1.4 mm (16G) Sheet Metal Powder Coated Enclosure with main circuit breaker (as per installed incoming cable and selected fan motor size) and accessories, to be included with AHU quoted price. The Enclosure shall be complied with Seven Tank Process and painted in Siemens Grey Colour Paint. The Electrical Panel Door Width shall not exceeds 600 mm (Single Leaf / Width). All the cable entries will be on the top of the panel & the cable knock-out will be made in factory by machine. The distribution of Electrical Power and provision of MPCB shall be provided with in this panel as per the AHU Fan Quantity and internal lighitng . The control cabling for door interlocks and marine light operation will be included in the scope of work. The electrical panel shall have potential free relay contacts along with suitably rated power contactor for interlocking with fire alarm control module. The electrical starter panel shall have necessary relay and potential free contacts along with suitably power contactor for the following BMS provisions: (1) Auto / Manual command, (2) ON / OFF command (3) Run status, (4) Trip Status. Vendor shall provide a seperate BMS terminal block for external BMS vendor to terminate their one set cabels for AHU on/off command, Fan speed, fan speed feedback, run status and trip status & As there would be multiple number of fans, all internal interlock / intercommunication cabling between multiple fans and relays shall be considered inside the panels. The panel shall be provided with a common potentio meter for manual fan adjustment, interlocked with Auto/manual switch. Please refer technical specifications for complete details & quote accordingly. The SLD & Control wiring GA drawing approval to be obtained from consultant before procurement. AHU shall be disengaged when the access door is opened, and it shall perform on normal mode when trip reset on the control panel after closing the access door. The panel shall be provided with additional circuit breakers for duct-mounted heater bank, control panel to have stepless control, interlocks for safe fan operation incase of over-heat & no-flow. The panel should match the description as part of electrical starter panel. | [12 empty] | 0 | 0
20.01 | TREATED FRESH AIR PANEL | IEC PANEL | 30000 CMH, 250 Pa External Static pressure | Q10: 2 | 2 | EACH | 0 | 0 | 0 | 0 | 0 | We have included starter panel along with air washer
20.02 | TREATED FRESH AIR PANEL | IEC PANEL | 31500 CMH, 250 Pa External Static pressure | Q10: 2 | 2 | EACH | 0 | 0 | 0 | 0 | 0
20.03 | TREATED FRESH AIR PANEL | IEC PANEL | 7000 CMH, 100 Pa External Static pressure | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
21 | CHW-EQUIPMENT | DE-HUMIDIFIER | DE-HUMIDIFIER UNIT : Supply, installation, testing and commissioning of factory fabricated 50-mm thick double skin unit comprising of pre-cooling coil ,dessicant wheel to handle the mixture of fresh air and 30% of total volume flow rate, electric heaters for re-generation, post cooling coil, complete set of DIDW fans with EFF-1 motors, inbuilt micro-processor control panel with ncessary sensors, External BMS communication via Modbus over MSTP, Supply Air Quantity 1250 CMH, 200 Pa external static pressure as per technical specifications.- | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
22 | CHW-EQUIPMENT | MID STATIC FCU | MID STATIC FAN COIL UNITS: Design, Supply, installation, testing and commissioning of factory made the following capacity, single skinned ceiling suspended , internally lined for acoustic performance, chilled water type fan coil unit consisting of Cabinet, Pre-filters (10 microns) section with filter frame, chilled water cooling coil(Min 4 row) with 1.2-mm thick Stainless steel (SS 304) insulated tilted condensate drain pan with 9-mm thick Nitrile rubber bottom Insulation, DIDW forward curved direct driven fans, fan motors, necessary mounting Arrangement, Fire retardant flexible connection, condensate drain pump, necessary supports as per the specification and drawings with rubber grommet. The quote price shall include valve kit with inbuilt 2-way PIBCV 24 AC/DC power, 0-10 V DC control (or) external mounted 2-way PIBCV 24 AC/DC power, 0-10 V DC control with actuators (Similar to the one supplied for the AHU's) and power and control wiring to Fan coil units control module with plugtop. External drain pan shall cover the valve station set. | [12 empty] | 0 | 0
22.01 | CHW-EQUIPMENT | MID STATIC FCU | 0.88 TR, 510 CMH 30 Pa External static pressure | [10 empty] | QRO | EACH | 51382 | 5000 | 0 | 0 | 0
22.02 | CHW-EQUIPMENT | MID STATIC FCU | 1.1 TR, 680 CMH 30 Pa External static pressure | Q3: 1; Q7: 2 | 3 | EACH | 51382 | 5000 | 154146 | 15000 | 169146
22.03 | CHW-EQUIPMENT | MID STATIC FCU | 1.5 TR, 1020 CMH 30 Pa External static pressure | [10 empty] | QRO | EACH | 54797 | 5000 | 0 | 0 | 0
22.04 | CHW-EQUIPMENT | MID STATIC FCU | 1.87 TR, 1300 CMH 30 Pa External static pressure | [10 empty] | QRO | EACH | 63181 | 5000 | 0 | 0 | 0
22.05 | CHW-EQUIPMENT | MID STATIC FCU | 2.0 TR, 1360 CMH, 30 Pa External static pressure | Q5: 1; Q6: 16; Q7: 26; Q8: 30 | 73 | EACH | 63181 | 5000 | 4612213 | 365000 | 4977213
23 | CHW-EQUIPMENT | HIGH STATIC FCU | HIGH STATIC FAN COIL UNITS: Design, Supply, installation, testing and commissioning of factory made the following capacity, single skinned ceiling suspended , internally lined for acoustic performance, chilled water type fan coil unit consisting of Cabinet, Pre-filters (10 microns) section with filter frame, chilled water cooling coil(Min 4 row) with 1.2-mm thick Stainless steel (SS 304) insulated tilted condensate drain pan with 9-mm thick Nitrile rubber bottom Insulation, DIDW forward curved direct driven fans, fan motors, necessary mounting Arrangement, Fire retardant flexible connection, Room temperature sensor & Cordless remote controller, condensate drain pump, necessary supports as per the specification and drawings with rubber grommet. The quote price shall include inbuilt 2-way PIBCV 24 AC/DC power, 0-10 V DC control (or) external mounted 2-way PIBCV 24 AC/DC power, 0-10 V DC control with actuators (Similar to the one supplied for the AHU's) and control wiring to Fan coil units control module. External drain pan shall cover the valve station set. The quote price shall include the cost of plug top with socket, additional circuit breaker for PIBCV 24 AC/DC power, 0-10 V DC control and power & control cabling shall also be added.. | [12 empty] | 0 | 0
23.01 | CHW-EQUIPMENT | HIGH STATIC FCU | 1.1 TR, 760 CMH 70 Pa External static pressure | [10 empty] | 1 | EACH | 56598 | 5000 | 56598 | 5000 | 61598 | bar: Q3
23.02 | CHW-EQUIPMENT | HIGH STATIC FCU | 1.5 TR, 1140 CMH 70 Pa External static pressure | [10 empty] | QRO | EACH | 64981 | 5000 | 0 | 0 | 0
23.03 | CHW-EQUIPMENT | HIGH STATIC FCU | 1.87 TR, 1360 CMH 70 Pa External static pressure | [10 empty] | QRO | EACH | 66844 | 5000 | 0 | 0 | 0
23.04 | CHW-EQUIPMENT | HIGH STATIC FCU | 2.0 TR, 1500 CMH, 70 Pa External static pressure | Q3: 1; Q4: 2; Q6: 4; Q8: 6 | 13 | EACH | 73365 | 5000 | 953745 | 65000 | 1018745
23.05 | CHW-EQUIPMENT | HIGH STATIC FCU | 2.5 TR, 1700 CMH, 70 Pa External static pressure | Q6: 2; Q8: 2; Q9: 2 | 6 | EACH | 75476 | 5000 | 452856 | 30000 | 482856
23.06 | CHW-EQUIPMENT | HIGH STATIC FCU | 3.0 TR, 2040 CMH, 70 Pa External static pressure |  |  | 1 | 1 | 1 |  | 10 | 8 | 3 |  | 24 | EACH | 77960 | 5000 | 1871040 | 120000 | 1991040
23 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | CEILING MOUNTING TYPE FOUR WAY CASSETTE UNITS (CHILLED WATER TYPE): Supply, installation, testing and commissioning of the following capacity, ceiling mounting type, chilled water type cassette unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, fresh air port, chilled water cooling coil,tilted Insulated drain tray, Prefilters, Room temperature sensor & Cordless remote controller, Control module self-diagnostic features, Inbuilt condensate drain pump, necessary supports as per the specification and drawings with rubber grommet. The quote price shall include valve kit with inbuilt 2-way PIBCV 24 AC/DC power, 0-10 V DC control (or) external mounted 2-way PIBCV 24 AC/DC power, 0-10 V DC control ON/OFF type with actuators and control wiring to Cassette units control module. The vendor shall consider plug top with socket with necessary power and control cable. External drain pan shall cover the valve station set. | [12 empty] | 0 | 0
23.01 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 1.07 TR, 630 CMH | [10 empty] | QRO | EACH | 53866 | 5625 | 0 | 0 | 0
23.02 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 1.6 TR, 1600 CMH | [10 empty] | QRO | EACH | 65665 | 5625 | 0 | 0 | 0
23.03 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 2.1 TR, 1250 CMH | Q1: 2; Q3: 2; Q4: 4; Q6: 4; Q7: 4 | 16 | EACH | 65665 | 5625 | 1050640 | 90000 | 1140640
23.04 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 2.3 TR, 1600 CMH | [10 empty] | QRO | EACH | 65665 | 5625 | 0 | 0 | 0
23.05 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 3 TR, 2000 CMH | Q1: 1; Q3: 1; Q8: 2 | 4 | EACH | 70570 | 5625 | 282280 | 22500 | 304780
23.06 | CHW-EQUIPMENT | 4 WAY CASSETTE UNIT | 3.6 TR, 2550 CMH | Q6: 2; Q7: 1; Q9: 2 | 5 | EACH | 75538 | 5625 | 377690 | 28125 | 405815
24 | CHW-EQUIPMENT | COMPACT CASSETTE UNIT | CEILING MOUNTING TYPE COMPACT CASSETTE UNITS (CHILLED WATER TYPE): Supply, installation, testing and commissioning of the following capacity, ceiling mounting type, chilled water type compact cassette unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, fresh air port, chilled water cooling coil, Insulated drain tray, Prefilters, Room temperature sensor & Cordless remote controller, Control module self-diagnostic features, Inbuilt condensate drain pump, necessary supports as per the specification and drawings with rubber grommet. The quote price shall include valve kit with inbuilt 2-way PIBCV 24 AC/DC power, 0-10 V DC control valve with modulating tight shut-off actuators and control wiring to Cassette units control module. External drain pan shall cover the valve station set. | [12 empty] | 0 | 0
24.01 | CHW-EQUIPMENT | COMPACT CASSETTE UNIT | 0.85 TR, 510 CMH | [10 empty] | QRO | EACH | 53182 | 5625 | 0 | 0 | 0
24.02 | CHW-EQUIPMENT | COMPACT CASSETTE UNIT | 1.05 TR, 680 CMH | 8 |  | 1 | 2 |  |  | 16 | 7 | 1 |  | 35 | EACH | 53182 | 5625 | 1861370 | 196875 | 2058245
24.03 | CHW-EQUIPMENT | COMPACT CASSETTE UNIT | 1.25 TR, 850 CMH | [10 empty] | QRO | EACH | 67465 | 5625 | 0 | 0 | 0
24 | CHW-EQUIPMENT | ONE WAY CASSETTE UNIT | CEILING MOUNTING TYPE ONE WAY CASSETTE UNITS (CHILLED WATER TYPE): Supply, installation, testing and commissioning of the following capacity, ceiling mounting type, chilled water type cassette unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, fresh air port, chilled water cooling coil, Insulated drain tray, Prefilters, Room temperature sensor & Cordless remote controller, Control module self-diagnostic features, Inbuilt condensate drain pump, necessary supports as per the specification and drawings with rubber grommet. The quote price shall include valve kit with inbuilt 2-way PIBCV 24 AC/DC power, 0-10 V DC control valve with modulating tight shut-off actuators and control wiring to Cassette units control module. The vendor shall consider plug top with socket with necessary power and control cable. | [12 empty] | 0 | 0
24.01 | CHW-EQUIPMENT | ONE WAY CASSETTE UNIT | 0.86 TR, 510 CMH | Q1: 1; Q3: 2; Q7: 1 | 4 | EACH | 53182 | 5625 | 212728 | 22500 | 235228
24.02 | CHW-EQUIPMENT | ONE WAY CASSETTE UNIT | 1.07 TR, 630 CMH | [10 empty] | 1 | EACH | 53182 | 5625 | 53182 | 5625 | 58807 | bar: Q1
24.03 | CHW-EQUIPMENT | ONE WAY CASSETTE UNIT | 1.62 TR, 1600 CMH | [10 empty] | QRO | EACH | 67465 | 5625 | 0 | 0 | 0
25 | CHW-EQUIPMENT | CHW - HI WALL UNIT | CHW HI WALL UNIT: Supply, installation, testing and commissioning of the following capacity, HI-WALL mounting type, chilled water fan coil unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, chilled water cooling coil (minimum 3-4 rows), in-built pressure independent motorized two way control valve (PIBCV 24 AC/DC power, 0-10 V DC control ) ON/OFF type of approved make in the specifications, Insulated drain tray, Prefilters, Cordless remote controller, necessary supports as per the specification and drawings. The vendor shall quote along with drain pump. The quote price shall include inbuilt valve kit with 2-way PIBCV 24 AC/DC power, 0-10 V DC control valve with modulating tight shut-off actuators and control wiring to Cassette units control module. The vendor shall consider plug top with socket with necessary power and control cable. | [12 empty] | 0 | 0
25.01 | CHW-EQUIPMENT | CHW - HI WALL UNIT | 0.84 TR, 510 CMH | [10 empty] | QRO | EACH | 44077 | 0 | 0 | 0 | 0
25.02 | CHW-EQUIPMENT | CHW - HI WALL UNIT | 1.07 TR, 630 CMH | Q3: 3; Q4: 2; Q6: 1; Q7: 2; Q8: 1 | 9 | EACH | 44077 | 3125 | 396693 | 28125 | 424818
25.03 | CHW-EQUIPMENT | CHW - HI WALL UNIT | 1.42 TR, 1020 CMH | Q5: 2; Q9: 2 | 4 | EACH | 48383 | 3125 | 193532 | 12500 | 206032
25.04 | CHW-EQUIPMENT | CHW - HI WALL UNIT | 2.0TR, 1435 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
25.05 | CHW-EQUIPMENT | CHW - HI WALL UNIT | 2.5TR, 1750 CMH | Q3: 1; Q5: 2; Q9: 2 | 5 | EACH | 77915 | 3125 | 389575 | 15625 | 405200
26 | CHW-EQUIPMENT | CHW PAC | PRECISION AC UNITS: (DX & CHW TYPE) Design, Manufacture, Supply, Installation, Testing, and Commissioning of Self-contained, Vertical, factory assembled, pre-wired, pre-piped precision air-conditioning units; consisting of GI Powder coated insulated cabinet, high efficiency direct drive backward curved fans each running with EC motors of TOP discharge air delivery, Inverter Scroll Compressors, Condensing units, DX coil & CHW coil, with inbuilt Microprocessor controller with display, inbuilt motorized damper with control in return air, inbuilt water leak detector, electric strip heater with heater bank and step control, filters, full charge of refrigerant and with necessary accessories. The price should include the cost of starter panel. Controller shall start the CHW circuit based on load requirement in sequence. The units shall operate in Lead/Lag equal runtime basis. If the lead circuit CHW fails to start or fails during continuous running, the PAC unit master controller shall start the stand-by unit without any manual intervention. All unit shall act as master unit. Vendor should include the cost of the extended kit for additional length of refrigerant piping. Vendor should select the PAC units which shall be integrate with BMS. Vendor should select the unit considering the deration calculation due to the Ambient temperature (Actual capacity at 40 Deg C) and refrigerant pipe length as per the "Annexure-A ". Please refer the technical specification for more details. Each circuit to act as independant unit and to meet the full capacity as stated. THe unit should be able to communicate and control through Modbus in-built. | [12 empty] | 0 | 0
26.01 | CHW-EQUIPMENT | CHW PAC | 12.0 TR, 16,320CMH | [10 empty] | 1 | EACH | 1388970 | 31250 | 1388970 | 31250 | 1420220 | bar: Q8
26.02 | CHW-EQUIPMENT | CHW PAC | PRECISION AC UNITS - ACCESSORIES: Design, Manufacture, Supply, Installation, Testing, and Commissioning of local supply items for above described PAC. The price shall include the cost of indoor height-adjustable units stands (painted MS angle frames), vibration isolators, base plates and outdoor unit stand | [10 empty] | 1 | EACH | 17250 | 4375 | 17250 | 4375 | 21625 | bar: Q8
27 | VRF EQUIPMENT | VRF OUTDOOR UNIT | VARIABLE REFRIGERANT FLOW OUTDOOR UNITS (VRF ODU) Supply, installation, testing and commissioning of the following capacity, Variable Refrigerant Flow Outdoor Unit consisting of GI Powder coated Cabinet, Inverter driven Compressors (i.e.., all the compressor should have inverter), (Invertor Scroll / Rotary ) per ODU, Finned tube copper Condenser Coil, Condenser fans with motors with variable speed controller, System Controller with Modbus MSTP integrator, Electrical components (Power Contactors, Control Relays, Overload Relays, Wiring etc.,) necessary mounting brackets, Vibration Isolators. The VRF System shall use R410A as refrigerant. The system shall include full charge of refrigerant. The vendor shall provide local isolator for outdoor units. If multiple outdoor modules are used, HVAC vendor should provide an electrical panel (IP 55, outdoor mountable) with Suitable incomer & outgoings breakers for outdoor units. The outdoor units shall be suitable for 415 ± 5 V, 3- phase power supply and all the compressors shall be rated for year-round continuous-duty (24 x 7 x 365) operation. The Minimum COP shall be maintained 3.51 / EER of 12 at AHRI condition for whole VRF system. The bidder can visit the site and can include cost of necessary scaffolding required to install the outdoor units. The HVAC Vendor is responsible to make the selection of suitable indoor units from their available product range considering capacity loss due to pipe length and level difference between VRF IDUs & VRF ODUs, Indoor/Outdoor design conditions and permissible diversity factor etc., Vendor to calculate the deration and fillup the required details as per "Annexure - A". The outdoor units shall be suitable for 415 ± 5 V, 3- phase power supply and all the compressors shall be rated for year-round continuous-duty (24 x 7 x 365) operation. The outdoor unit shall be sized to deliver following rated capacities which excludes de-rated capacity due to excess length of refrigeration pipes, change in indoor dry bulb & wet bulb temperature, suitable to ambient of 40°C. ODU | [12 empty] | 0 | 0
27.01 | VRF EQUIPMENT | VRF OUTDOOR UNIT | 25 TR | [10 empty] | 1 | EACH | 732979 | 43750 | 732979 | 43750 | 776729 | bar: Q10
27.02 | VRF EQUIPMENT | VRF OUTDOOR UNIT | 20 TR | [10 empty] | 1 | EACH | 628179 | 43750 | 628179 | 43750 | 671929 | bar: Q10
27.03 | VRF EQUIPMENT | VRF OUTDOOR UNIT | 8 TR | [10 empty] | 1 | EACH | 309010 | 15000 | 309010 | 15000 | 324010 | bar: Q10
27.04 | VRF EQUIPMENT | VRF OUTDOOR UNIT | 10 TR | Q9: 3 | 3 | EACH | 404172 | 15000 | 1212516 | 45000 | 1257516
28 | VRF EQUIPMENT | VRF INDOOR UNIT | HI-STATIC DUCT TYPE INDOOR UNITS (VRF IDU): Design, Manufacture, Supply, Installation, Testing, and Commissioning, of the following capacity, Ceiling mounting Duct type, Variable Refrigerant Flow Indoor Unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, Direct Expansion type cooling coil, Insulated drain tray, with inbuilt drain pump, Prefilters, Electronic Refrigerant Flow Control valve, Room temperature sensor & wired remote controller, Control module self-diagnostic features, necessary supports as per the specification and drawings. \ NOTE: Indicated Cooling & airflow Capacities of IDUs are the minimum requirement to meet the Designed indoor Conditions for the out door peak Weather Conditions as noted on drawing and Specification. The HVAC Vendor is responsible to make the selection of suitable indoor units from their available product range considering capacity loss due to pipe length and level difference between VRF ODUs etc. | [12 empty] | 0 | 0
28.01 | VRF EQUIPMENT | VRF INDOOR UNIT | 6 TR - 3910 CMH | [10 empty] | QRO | EACH | 132221 | 6250 | 0 | 0 | 0
28.02 | VRF EQUIPMENT | VRF INDOOR UNIT | 8 TR - 5970 CMH | [10 empty] | QRO | EACH | 144296 | 6250 | 0 | 0 | 0
29 | VRF EQUIPMENT | VRF INDOOR UNIT | SLIM CEILING MOUNTED DUCT TYPE INDOOR UNITS (VRF IDU): Supply, installation, testing and commissioning of the following capacity, Ceiling mounting Duct type, Variable Refrigerant Flow Indoor Unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, Direct Expansion type cooling coil, Insulated drain tray, with in built drain pump, Prefilters, Electronic Refrigerant Flow Control valve, Room temperature sensor & necessary IR provision for cordless control, Control module self-diagnostic features, necessary supports as per the specification and drawings. NOTE: Indicated Cooling & airflow Capacities of IDUs are the minimum requirement to meet the Designed indoor Conditions for the out door peak Weather Conditions as noted on drawing and Specification. The HVAC Vendor is responsible to make the selection of suitable indoor units from their available product range considering capacity loss due to pipe length and level difference between VRF ODUs etc., | [12 empty] | 0 | 0
29.01 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.0 TR, 991 CMH, 50 Pa External Static Pressure | [10 empty] | QRO | EACH | 40693 | 6250 | 0 | 0 | 0
29.02 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.6.0 TR, 1080 CMH, 200 Pa External Static Pressure | [10 empty] | QRO | EACH | 44376 | 6250 | 0 | 0 | 0
29.03 | VRF EQUIPMENT | VRF INDOOR UNIT | 2.0 TR, 1170 CMH, 200 Pa External Static Pressure | [10 empty] | QRO | EACH | 45499 | 6250 | 0 | 0 | 0
29.04 | VRF EQUIPMENT | VRF INDOOR UNIT | 2.6.0 TR, 1500 CMH, 200 Pa External Static Pressure | [10 empty] | QRO | EACH | 52345 | 6250 | 0 | 0 | 0
29.05 | VRF EQUIPMENT | VRF INDOOR UNIT | 3.2 TR, 1921 CMH, 200 Pa External Static Pressure | [10 empty] | QRO | EACH | 54338 | 6250 | 0 | 0 | 0
29.06 | VRF EQUIPMENT | VRF INDOOR UNIT | 4 TR, 2341 CMH, 200 Pa External Static Pressure | [10 empty] | QRO | EACH | 60798 | 6250 | 0 | 0 | 0
29.07 | VRF EQUIPMENT | VRF INDOOR UNIT | 4.5.0 TR, 2761 CMH, 150 Pa External Static Pressure | [10 empty] | 1 | EACH | 80166 | 6250 | 80166 | 6250 | 86416 | bar: Q1
30 | VRF EQUIPMENT | VRF INDOOR UNIT | CEILING MOUNTING TYPE CASSETTE UNITS (REGULAR): Supply, installation, testing and commissioning of the following capacity, ceiling mounting type, Variable Refrigerant Flow cassette Unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, fresh air port, Direct Expansion type cooling coil, Insulated drain tray, Prefilters, Electronic Refrigerant Flow Control valve, Room temperature sensor & Cordless remote controller, Infra red sensor, Control module self-diagnostic features, Inbuilt condensate drain pump, necessary supports . The VRF System shall use R410A as refrigerant. | [12 empty] | 0 | 0
30.01 | VRF EQUIPMENT | VRF INDOOR UNIT | 1 TR, 780 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
30.02 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.3 TR, 900 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
30.03 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.6 TR, 960 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
30.04 | VRF EQUIPMENT | VRF INDOOR UNIT | 2 TR, 1141 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
30.05 | VRF EQUIPMENT | VRF INDOOR UNIT | 2.5 TR, 1261 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
31 | VRF EQUIPMENT | VRF INDOOR UNIT | CEILING MOUNTING TYPE CASSETTE UNITS (COMPACT): Supply, installation, testing and commissioning of the following capacity, ceiling mounting type, Variable Refrigerant Flow cassette Unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, fan motors, fresh air port, Direct Expansion type cooling coil, Insulated drain tray, Prefilters, Electronic Refrigerant Flow Control valve, Room temperature sensor & Cordless remote controller, Infra red sensor, Control module self-diagnostic features, Inbuilt condensate drain pump, necessary supports. The VRF System shall use R410A as refrigerant. | [12 empty] | 0 | 0
31.01 | VRF EQUIPMENT | VRF INDOOR UNIT | 0.8 TR, 540 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
31.02 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.3 TR, 660 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
31.03 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.6 TR, 838 CMH | [10 empty] | QRO | EACH | 0 | 0 | 0 | 0 | 0
32 | VRF EQUIPMENT | VRF INDOOR UNIT | WALL MOUNTING TYPE HIWALL UNITS (VRF IDU): Design, Manufacture, Supply, Installation, Testing, and Commissioning of the following capacity, wall mounting type, Variable Refrigerant Flow hi-wall Unit consisting of Thermo plastic Cabinet, Dynamically balanced centrifugal blowers, auto-swinging louvers for four way air distribution type, fan motors, Direct Expansion type cooling coil, Insulated drain tray, Prefilters, Electronic Refrigerant Flow Control valve, Room temperature sensor & Cordless remote controller, Control module self-diagnostic features, necessary supports as per the specification and drawings. Price shall include the cost of suitable drain pump with necessary cabling, hose etc. as required .NOTE: Indicated Cooling & airflow Capacities of IDUs are the minimum requirement to meet the Designed indoor Conditions for the out door peak Weather Conditions as noted on the drawings and specification. The HVAC Vendor is responsible to make the selection of suitable indoor units from their available product range to meet both TR & airflow rate and considering capacity loss due to pipe length and level difference between VRF IDUs & VRF ODUs and Indoor/Outdoor design conditions etc. | [12 empty] | 0 | 0
32.01 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.0 TR, 510 CMH | [10 empty] | QRO | EACH | 17350 | 3125 | 0 | 0 | 0
32.02 | VRF EQUIPMENT | VRF INDOOR UNIT | 1.5 TR, 721 CMH | [10 empty] | QRO | EACH | 19442 | 3125 | 0 | 0 | 0
32.03 | VRF EQUIPMENT | VRF INDOOR UNIT | 2 TR, 1141 CMH | [10 empty] | QRO | EACH | 26948 | 3125 | 0 | 0 | 0
32.04 | VRF EQUIPMENT | VRF INDOOR UNIT | 2.5 TR, 1275 CMH | [10 empty] | 1 | EACH | 34918 | 3125 | 34918 | 3125 | 38043 | bar: Q3
32.05 | VRF EQUIPMENT | VRF INDOOR UNIT | 3 TR, 1530 CMH | Q4: 2; Q6: 2; Q9: 3 | 7 | EACH | 43068 | 3125 | 301476 | 21875 | 323351
33 | VRF EQUIPMENT | VRF INTEGRATOR | VRF INTEGRATOR: Design, Manufacture, Supply, Installation, Testing, and Commissioning of the VRF Modbus over IP interface with IP55 rated enclosure ,the cost of necessary power and control cabling shall be included between IDU's, ODU's and Interface. The vendor shall consider the necessary item which make the outdoor unit suitable for Modbus interface. The minimum connecting ODU shall be 20 Nos and IDU shall be 50 nos. | Q9: 2; Q10: 2 | 4 | EACH | 235946 | 6250 | 943784 | 25000 | 968784
33 | VRF EQUIPMENT | VRF AHU KIT | VRF AHU KIT: Supply, installation, testing and commissioning of Electronic Type Expansion Kit, Communication PCB with Sensors, Self Diagnostic Type Digital Thermostat, corded remote, with necessary accessories etc. as required for following Air Handling Unit to contol the DX Coil over VRF and communicate over Modbus for control. The kit should be matched as per the DX Coil requirement. | [10 empty] | 12 | EACH | 35838 | 10625 | 430056 | 127500 | 557556
34 | VRF PIPING & ACCESSORIES | VRF COMMUNICATION CABLE | VRF COMMUNICATION CABLE: Supply, installation, testing and commissioning of communication cabling to connect VRF units and Integrator. The communication cable shall be run through the IS: 9537 Part 3, BS: EN 61386 – 21 for FRLS UPVC conduits, IS: 3419 and BS: 4607 for UPVC fittings of Heavy duty conduits. The cable quantity shall be claimed only for ODU and Integrator | Q9: 50; Q10: 50 | 100 | METER | 162 | 38 | 16200 | 3800 | 20000
35 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | VRF / DX REFRIGERANT PIPING & ELECTRICAL POWER/CONTROL CABLING: Supply, installation, testing and commissioning of 1.2mm thick hard drawn (below 6HP soft drawn is acceptable) copper refrigerant pipes for VRF Indoors and Outdoors with necessary copper fittings, closed cell nitrile tubular insulation (Class-O) with aluminium foil, T-connectors, refnet joints / pipe branching kits, and silver-soldered joints to withstand minimum 3000 kPa pressure. The pipe sizes shall be selected according to the equipment's capacities. The vendor shall also provide the Power/Control cabling required between the IDUs & ODUs.The price shall include power cabling for outdoor units, communication cabling between IDU's and ODu's and wired remote cabling for IDU's in IS: 9537 Part 3, BS: EN 61386 – 21 for FRLS UPVC conduits, IS: 3419 and BS: 4607 for UPVC fittings of Heavy duty conduits. Pipe quantity will be provided by vendor. The quoted price shall include the cost of minor works like wall opening & closing to run the refrigerant pipes and cable tray. | [12 empty] | 0 | 0
35.01 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 41.3 mm dia with 19 mm thick insulation | Q10: 70 | 70 | METER | 2533 | 188 | 177310 | 13160 | 190470
35.02 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 34.92 mm dia with 19 mm thick insulation | [10 empty] | QRO | METER | 2194 | 188 | 0 | 0 | 0
35.03 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 31.75 mm dia with 19 mm thick insulation | [10 empty] | QRO | METER | 2022 | 188 | 0 | 0 | 0
35.04 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 28.57 mm dia with 19 mm thick insulation | Q2: 15; Q10: 15 | 30 | METER | 1848 | 188 | 55440 | 5640 | 61080
35.05 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 25.4 mm dia with 19 mm thick insulation | Q4: 5; Q10: 30 | 35 | METER | 1673 | 188 | 58555 | 6580 | 65135
35.06 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 22.2 mm dia with 19 mm thick insulation | Q4: 50; Q6: 60; Q8: 35 | 145 | METER | 1498 | 188 | 217210 | 27260 | 244470
35.07 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 19.05 mm dia with 19 mm thick insulation | Q1: 60; Q8: 20; Q9: 20; Q10: 70 | 170 | METER | 1323 | 188 | 224910 | 31960 | 256870
35.08 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 15.87 mm dia with 19 mm thick insulation | Q4: 30; Q6: 35; Q9: 60 | 125 | METER | 1157 | 188 | 144625 | 23500 | 168125
35.09 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 12.52 mm dia with 13 mm thick insulation |  | 15 | 80 | 31 | 54 |  | 45 | 55 | 20 | 45 | 345 | METER | 844 | 188 | 291180 | 64860 | 356040
35.1 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 9.52 mm dia with 13 mm thick insulation | Q1: 60; Q4: 80; Q6: 94; Q8: 51; Q9: 80 | 365 | METER | 736 | 188 | 268640 | 68620 | 337260
35.11 | VRF PIPING & ACCESSORIES | VRF/DX REFRIGERANT PIPING | 6.35 mm dia with 13 mm thick insulation |  |  | 80 | 25 | 55 |  | 45 | 55 | 20 |  | 280 | METER | 591 | 188 | 165480 | 52640 | 218120
35.12 | VRF PIPING & ACCESSORIES | CABLE TRAY | 300 mm wide GI slotted cable tray 1.2mm thick with necessary clamps for refrigerant pipe support. | Q6: 80; Q7: 40; Q8: 100; Q9: 80 | 300 | METER | 708 | 250 | 212400 | 75000 | 287400
35.13 | VRF PIPING & ACCESSORIES | CABLE TRAY | 200 mm wide GI slotted cable tray 1.2mm thick with necessary clamps for refrigerant pipe support. | Q3: 100; Q4: 100; Q5: 45 | 245 | METER | 556 | 250 | 136220 | 61250 | 197470
35.14 | VRF PIPING & ACCESSORIES | CABLE TRAY | 100 mm wide GI slotted cable tray 1.2mm thick with necessary clamps for refrigerant pipe support. | Q1: 50; Q2: 10 | 60 | METER | 404 | 250 | 24240 | 15000 | 39240
35.15 | VRF PIPING & ACCESSORIES | CABLE TRAY | 300 mm wide GI slotted cable tray 1.2mm thick with necessary clamps and 0.4 mm (26 G) GI sheet cover for refrigerant pipe support. (only in shafts & exposed areas) | Q10: 115 | 115 | METER | 1125 | 250 | 129375 | 28750 | 158125
35.16 | VRF PIPING & ACCESSORIES | CABLE TRAY | 200 mm wide GI slotted cable tray 1.2mm thick with necessary clamps and 0.4 mm (26 G) GI sheet cover for refrigerant pipe support. (only in shafts & exposed areas) | [10 empty] | QRO | METER | 851 | 250 | 0 | 0 | 0
35.17 | VRF PIPING & ACCESSORIES | CABLE TRAY | 100 mm wide GI slotted cable tray 1.2mm thick with necessary clamps and 0.4 mm (26 G) GI sheet cover for refrigerant pipe support. (only in shafts & exposed areas) | [10 empty] | QRO | METER | 578 | 250 | 0 | 0 | 0
36 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | CHILLED WATER PIPING: Supply, installation and testing of painted MS 'C' class pipes. The necessary piping supports to be provided as mentioned in the specification. The piping flange connection bolts and nuts should be of hot dipped galvanised. Please refer technical specifications for complete details and scope & quote accordingly. The vendor shall consider neccessary provisions for sensors & Gauges. Please include the cost of pressure testing, any shut-down work, flushing works, etc.The vendor shall consider neccessary provisions for sensors & Gauges. The support for pipes to be with PuF saddles and angles/channels to be of MS black painted with doublel nut prtoection. The edges of the supports to be cold galvanized. The pipe has to be protected by primer before installaiton. | [12 empty] | 0 | 0
36.01 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 300 mm dia | Q10: 220 | 220 | METER | 7000 | 3000 | 1540000 | 660000 | 2200000
36.02 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 250 mm dia | Q10: 490 | 490 | METER | 5902 | 2500 | 2891980 | 1225000 | 4116980
36.03 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 200 mm dia | Q10: 110 | 110 | METER | 4608 | 1750 | 506880 | 192500 | 699380
36.04 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 150 mm dia | Q10: 70 | 70 | METER | 2205 | 1125 | 154350 | 78750 | 233100
36.05 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 125 mm dia | Q9: 5 | 5 | METER | 1869 | 938 | 9345 | 4690 | 14035
36.06 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 100 mm dia | Q8: 5; Q9: 150; Q10: 70 | 225 | METER | 1512 | 625 | 340200 | 140625 | 480825
36.07 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 80 mm dia | 10 |  | 45 |  | 80 | 70 | 10 | 10 | 160 |  | 385 | METER | 1212 | 500 | 466620 | 192500 | 659120
36.08 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 65 mm dia | 180 |  | 50 | 60 | 5 | 65 | 100 | 90 | 5 |  | 555 | METER | 990 | 406 | 549450 | 225330 | 774780
36.09 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 50 mm dia | 10 | 40 | 110 | 130 | 10 | 110 | 465 | 450 | 130 |  | 1455 | METER | 769 | 313 | 1118895 | 455415 | 1574310
36.1 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 40 mm dia |  |  | 55 | 10 | 90 | 70 | 70 | 60 | 60 |  | 415 | METER | 619 | 250 | 256885 | 103750 | 360635
36.11 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 32 mm dia | 20 |  | 180 | 170 | 250 | 240 | 115 | 120 | 230 | 35 | 1360 | METER | 505 | 200 | 686800 | 272000 | 958800
36.12 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 25 mm dia | 20 |  | 110 | 120 | 100 | 80 | 150 | 130 | 175 | 15 | 900 | METER | 399 | 156 | 359100 | 140400 | 499500
36.13 | CHW PIPING & ACCESSORIES WORKS | CHILLED WATER PIPING | 20 mm dia | 135 |  | 135 | 120 | 250 | 300 | 410 | 550 | 65 |  | 1965 | METER | 326 | 125 | 640590 | 245625 | 886215
37 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | Supply, Installation, Testing and Commissioning of thermal insulation on chilled water pipe on the following heavy Class "C" MS pipes and fitting with 50 mm thick, Thermal condcutivity 0.030 W/(m-K) @ 20 Deg C , 24 kg/cum density TF quality expanded polystyrene pre-formed pipe sections upto 80 mm dia pipes and 75 mm thick insulation for above 80 mm dia pipes finished with air-tight leak-proof alkathene vapour barrier, 22 G GI chicken wire mesh wrapping. | [12 empty] | 0 | 0
37.01 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 300 mm dia | [10 empty] | QRO | METER | 1249 | 1065 | 0 | 0 | 0
37.02 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 250 mm dia | Q10: 490 | 490 | METER | 1090 | 1035 | 534100 | 507150 | 1041250
37.03 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 200 mm dia | Q10: 110 | 110 | METER | 926 | 825 | 101860 | 90750 | 192610
37.04 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 150 mm dia | Q10: 70 | 70 | METER | 760 | 765 | 53200 | 53550 | 106750
37.05 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 125 mm dia | Q9: 5 | 5 | METER | 683 | 743 | 3415 | 3715 | 7130
37.06 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 100 mm dia | Q8: 5; Q9: 150; Q10: 70 | 225 | METER | 602 | 690 | 135450 | 155250 | 290700
37.07 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 80 mm dia | 10 |  | 45 |  | 80 | 70 | 10 | 10 | 160 |  | 385 | METER | 298 | 645 | 114730 | 248325 | 363055
37.08 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 65 mm dia | 180 |  | 50 | 60 | 5 | 65 | 100 | 90 | 5 |  | 555 | METER | 272 | 570 | 150960 | 316350 | 467310
37.09 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 50 mm dia | 10 | 40 | 110 | 130 | 10 | 110 | 465 | 450 | 130 |  | 1455 | METER | 235 | 540 | 341925 | 785700 | 1127625
37.1 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 40 mm dia |  |  | 55 | 10 | 90 | 70 | 70 | 60 | 60 |  | 415 | METER | 214 | 405 | 88810 | 168075 | 256885
37.11 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 32 mm dia | 20 |  | 180 | 170 | 250 | 240 | 115 | 120 | 230 | 35 | 1360 | METER | 201 | 365 | 273360 | 496400 | 769760
37.12 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 25 mm dia | 20 |  | 110 | 120 | 100 | 80 | 150 | 130 | 175 | 15 | 900 | METER | 182 | 338 | 163800 | 304200 | 468000
37.13 | CHW PIPING & ACCESSORIES WORKS | PIPE INSULATION | 20 mm dia | 135 |  | 135 | 120 | 250 | 300 | 410 | 550 | 65 |  | 1965 | METER | 167 | 338 | 328155 | 664170 | 992325
38 | CHW PIPING & ACCESSORIES WORKS | ALUMINIUM CLADDING | ALUMINIUM CLADDING: Supply, installation, testing and commissioning of 0.8 mm thick aluminium sheet metal as cladding as shown in approved design drawings and sample with necessary arrangements complying to IS standards. Please refer Specifications for more details. | Q10: 1200 | 1200 | m2 | 888 | 300 | 1065600 | 360000 | 1425600
39 | CHW PIPING & ACCESSORIES WORKS | ALUMINIUM CLADDING | ALUMINIUM CLADDING: Supply, installation, testing and commissioning of 0. 6 mm thick aluminium sheet metal as cladding as shown in approved design drawings and sample with necessary arrangements complying to IS standards. Please refer Specifications for more details. | Q10: 200 | 200 | m2 | 671 | 300 | 134200 | 60000 | 194200
40 | CHW PIPING & ACCESSORIES WORKS | CONDENSER WATER PIPING | CONDENSER WATER PIPING WITH FRP COATING: Supply, installation, testing and commissioning of FRP Coating 350 Micron Class O in nearby cooling tower pipe around 3m distance as shown in approved design drawings. Please refer Specifications for more details. | Q10: 150 | 150 | METER | 468 | 125 | 70200 | 18750 | 88950
41 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | BUTTERFLY VALVES (CHW PIPING) : Supply, installation, testing & commissioning of Butterfly valves with 1600kPaworking pressure,50 deg C maximum operating temperature, Cast iron body for DN 50 to 300, Ductile iron body for DN 350 plus, EPDM Seal, Stainless Steel 416 Shaft material, Nylon coated ductile iron, extended stem, lever lock handle, and wafer style for installation between flanges and confirming to IS:13095. Use Table"17" Flanges for connections with GI bolt nuts. Please refer technical specifications for complete details and scope & quote accordingly. Vendor shall consider PN16 pressure rating for all valves. | [12 empty] | 0 | 0
41.01 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 300 mm dia | [10 empty] | QRO | NOS | 32422 | 7500 | 0 | 0 | 0
41.02 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 250 mm dia | Q10: 14 | 14 | NOS | 24277 | 5625 | 339878 | 78750 | 418628
41.03 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 200 mm dia | Q10: 29 | 29 | NOS | 17199 | 4500 | 498771 | 130500 | 629271
41.04 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 150 mm dia | [10 empty] | QRO | NOS | 9106 | 2813 | 0 | 0 | 0
41.05 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 125 mm dia | Q9: 2; Q10: 8 | 10 | NOS | 8144 | 2344 | 81440 | 23440 | 104880
41.06 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 100 mm dia |  |  | 2 | 6 | 4 | 4 | 2 |  | 2 |  | 20 | NOS | 7070 | 1875 | 141400 | 37500 | 178900
41.07 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 80 mm dia | 2 |  | 4 | 2 | 2 |  |  | 8 | 2 |  | 20 | NOS | 5383 | 1500 | 107660 | 30000 | 137660
41.08 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 65 mm dia | Q3: 2; Q6: 2; Q7: 2; Q9: 6; Q10: 2 | 14 | NOS | 5160 | 1219 | 72240 | 17066 | 89306
41.09 | CHW PIPING & ACCESSORIES WORKS | BUTTERFLY VALVES | 50 mm dia | Q3: 4; Q5: 2; Q6: 4; Q10: 4 | 14 | NOS | 4852 | 938 | 67928 | 13132 | 81060
42 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | CHW AUTOMATIC BALANCING VALVES (CHW PIPING): Supply, installation, testing & commissioning of cartridge type automatic balancing valves of Cast-iron body with removable pre-set stainless steel cartridge, 800 kPa working pressure, 90 Deg C maximum operating temperature; Valves shall have connections with isolation device for portable differential pressure meter with integral seals, with extended temperature/pressure plugs; Flow accuracy shall be 5%+/-. For NPT 50mm and smaller: Bronze / Gun Metal body; Valves shall have connections isolation device for portable differential pressure meter with integral seals, Flow accuracy shall be 5%+/- .Use Table"17" Flanges for connections with GI bolt nuts. Please refer technical specifications for complete details and scope & quote accordingly. The complete valve assembly shall be insulated with similar insulation of chilled water piping. | [12 empty] | 0 | 0
42.01 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 250 mm dia | Q10: 2 | 2 | NOS | 297546 | 5625 | 595092 | 11250 | 606342 | We have quoted PIBCV Valves under this line item
42.02 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 200 mm dia | Q10: 4 | 4 | NOS | 297546 | 4500 | 1190184 | 18000 | 1208184
42.03 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 150 mm dia | [10 empty] | QRO | NOS | 205127 | 2813 | 0 | 0 | 0
42.04 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 125 mm dia | [10 empty] | QRO | NOS | 159065 | 2344 | 0 | 0 | 0
42.05 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 80 mm dia | [10 empty] | QRO | NOS | 92067 | 1500 | 0 | 0 | 0
42.06 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 65 mm dia | [10 empty] | QRO | NOS | 86484 | 1219 | 0 | 0 | 0
42.07 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 50 mm dia | [10 empty] | QRO | NOS | 70664 | 938 | 0 | 0 | 0
42.08 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 40 mm dia | [10 empty] | QRO | NOS | 52926 | 750 | 0 | 0 | 0
42.09 | CHW PIPING & ACCESSORIES WORKS | CHW AUTOMATIC BALANCING VALVES | 32 mm dia | [10 empty] | QRO | NOS | 34017 | 600 | 0 | 0 | 0
43 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | MOTORIZED BUTTERFLY VALVES: Supply, installation, testing & commissioning of Motorized Butterfly valves. Please refer technical Specifications for full scope and mode of measurement. Use Table"17" Flanges for connections with GI bolt nuts.Vendor shall consider PN16 pressure rating for all valves. Vendor shall include the necessary cost for Actuator, power cables & control cables etc., Actuator torque should be selected based on the design requirements. 230 V AC - 24V AC/DC operated, 0-10 V control, 0(2)-10 V feedback to BMS | [12 empty] | 0 | 0
43.01 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 300 mm dia | [10 empty] | QRO | NOS | 170462 | 7500 | 0 | 0 | 0
43.02 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 250 mm dia | Q10: 2 | 2 | NOS | 157437 | 5625 | 314874 | 11250 | 326124
43.03 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 200 mm dia | Q10: 2 | 2 | NOS | 126346 | 4500 | 252692 | 9000 | 261692
43.04 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 150 mm dia | [10 empty] | QRO | NOS | 116986 | 2813 | 0 | 0 | 0
43.05 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 125 mm dia | [10 empty] | QRO | NOS | 116118 | 2344 | 0 | 0 | 0
43.06 | CHW PIPING & ACCESSORIES WORKS | MOTORIZED BUTTERFLY VALVES | 50 mm dia | [10 empty] | QRO | NOS | 21710 | 938 | 0 | 0 | 0
44 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES W/ STRAINER | BALL VALVES : (CHW PIPING WITH INBUILT Y STAINER) : Supply, installation, testing & commissioning, 3-piece socket weldable type Ball Valves designed for Domestic, air-conditioning applications with female thread connections, Brass body material-nickel plated, extended shaft and nipple in steel; 1600 kPa working pressure; 50 deg C operating temperature as per Specification. The price shall include the cost of insulation similar to chilled water pipes. | [12 empty] | 0 | 0
44.01 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES W/ STRAINER | 40 mm dia | [10 empty] | 4 | NOS | 8914 | 750 | 35656 | 3000 | 38656 | bar: Q3; Q5 to Q6; Q9
44.02 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES W/ STRAINER | 32 mm dia | 4 |  | 4 | 2 | 2 | 3 | 3 | 2 | 12 | 3 | 35 | NOS | 8236 | 600 | 288260 | 21000 | 309260
44.03 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES W/ STRAINER | 25 mm dia | 6 |  | 5 | 3 | 6 | 7 | 4 | 1 | 9 | 1 | 42 | NOS | 6760 | 469 | 283920 | 19698 | 303618
44.04 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES W/ STRAINER | 20 mm dia | 12 | 2 | 14 | 15 |  | 36 | 64 | 62 | 24 |  | 229 | NOS | 5791 | 375 | 1326139 | 85875 | 1412014
45 | CHW PIPING & ACCESSORIES WORKS | NRV | NON-RETURN VALVES : Supply, installation, testing & commissioning of Ferrous-Alloy Check valve, Single / double plate, Flangeless body, rated for 1600kPa operating pressure. Use Table"17" Flanges for connections with GI bolt nuts. as per Specification. | [12 empty] | 0 | 0
45.01 | CHW PIPING & ACCESSORIES WORKS | NRV | 250 mm dia | Q10: 3 | 3 | NOS | 27245 | 5625 | 81735 | 16875 | 98610
45.02 | CHW PIPING & ACCESSORIES WORKS | NRV | 200 mm dia | Q10: 3 | 3 | NOS | 18952 | 4500 | 56856 | 13500 | 70356
45.03 | CHW PIPING & ACCESSORIES WORKS | NRV | 150 mm dia | Q10: 2 | 2 | NOS | 11806 | 2813 | 23612 | 5626 | 29238
45.04 | CHW PIPING & ACCESSORIES WORKS | NRV | 125 mm dia | [10 empty] | 1 | NOS | 10034 | 2344 | 10034 | 2344 | 12378 | bar: Q10
46 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | BALL VALVES : (CHW PIPING) : Supply, installation, testing & commissioning, 3-piece socket weldable type Ball Valves designed for Domestic, air-conditioning applications with female thread connections, Brass body material-nickel plated, extended shaft and nipple in steel; 1600 kPa working pressure; The price shall include the cost of insulation similar to chilled water pipes.Vendor shall consider PN16 pressure rating for all valves. | [12 empty] | 0 | 0
46.01 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | 40 mm dia | [10 empty] | 4 | NOS | 5245 | 750 | 20980 | 3000 | 23980 | bar: Q3; Q5 to Q6; Q9
46.02 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | 32mm dia | 4 |  | 4 | 2 | 2 | 3 | 3 | 2 | 12 | 3 | 35 | NOS | 4232 | 480 | 148120 | 16800 | 164920
46.03 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | 25 mm dia | 6 |  | 5 | 5 | 6 | 7 | 4 | 1 | 9 | 1 | 44 | NOS | 3084 | 375 | 135696 | 16500 | 152196
46.04 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | 20 mm dia | 12 | 2 | 14 | 15 | 2 | 36 | 64 | 62 | 24 | 2 | 233 | NOS | 2598 | 300 | 605334 | 69900 | 675234
46.05 | CHW PIPING & ACCESSORIES WORKS | BALL VALVES | 15 mm dia | 21 |  | 25 | 22 | 10 | 47 | 71 | 65 | 46 | 19 | 326 | NOS | 2369 | 225 | 772294 | 73350 | 845644
47 | CHW PIPING & ACCESSORIES WORKS | SUCTION GUIDE | PUMP SUCTION GUIDE: (CHW PIPING) : Supply, installation, testing & commissioning of MS body, SS 304 screen of 24 Gauge thickness and 3mm perforation. The suction guide shall be flanged type and shall be supplied with matching flanges, GI H bolts, nuts,washers,gaskets,fittings,accessories all complete as required 1600 kPa working pressure and with online in-built stain remover; The complete valve assembly shall be insulated with similar insulation of chilled water piping as per Specification. | [12 empty] | 0 | 0
47.01 | CHW PIPING & ACCESSORIES WORKS | SUCTION GUIDE | 250 mm dia | Q10: 3 | 3 | NOS | 47776 | 5625 | 143328 | 16875 | 160203
47.02 | CHW PIPING & ACCESSORIES WORKS | SUCTION GUIDE | 200 mm dia | Q10: 5 | 5 | NOS | 32684 | 4500 | 163420 | 22500 | 185920
47.03 | CHW PIPING & ACCESSORIES WORKS | SUCTION GUIDE | 150 mm dia | [10 empty] | QRO | NOS | 24883 | 2813 | 0 | 0 | 0
47.04 | CHW PIPING & ACCESSORIES WORKS | SUCTION GUIDE | 125 mm dia | Q10: 2 | 2 | NOS | 20058 | 2344 | 40116 | 4688 | 44804
48 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | Y-STRAINERS: (CHW PIPING) : Supply, installation, testing & commissioning of 1600 kPa working pressure; cast-iron body, flanged ends for DN65 and larger, threaded connections for DN 50 and smaller, bolted cover, perforated stainless-steel basket, and bottom drain connection. Use CS Hot dip Galvanized lab joint flanges conforming to IS 2062 to suit SS stub ends. SS stub ends conforming to ASTM A 403 Gr. WP 304-S, short neck with 125 AARH face finish to suit ANSI150 Lap joint flanges. The bolt length shall be suitable for fixing lock nut .The complete valve assembly shall be insulated with similar insulation of chilled water piping as per specification. | [12 empty] | 0 | 0
48.01 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 250 mm dia | [10 empty] | QRO | NOS | 31296 | 5625 | 0 | 0 | 0
48.02 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 200 mm dia | [10 empty] | QRO | NOS | 20219 | 4500 | 0 | 0 | 0
48.03 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 150 mm dia | [10 empty] | QRO | NOS | 13470 | 2813 | 0 | 0 | 0
48.04 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 125 mm dia | [10 empty] | QRO | NOS | 11540 | 2344 | 0 | 0 | 0
48.05 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 100 mm dia | [10 empty] | QRO | NOS | 9511 | 1875 | 0 | 0 | 0
48.06 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 80 mm dia | [10 empty] | 1 | NOS | 7277 | 1500 | 7277 | 1500 | 8777 | bar: Q5
48.07 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 65 mm dia | [10 empty] | 2 | NOS | 6387 | 1219 | 12774 | 2438 | 15212 | bar: Q3 to Q4
48.08 | CHW PIPING & ACCESSORIES WORKS | Y-STRAINER | 50 mm dia | [10 empty] | 2 | NOS | 5523 | 938 | 11046 | 1876 | 12922 | bar: Q2; Q4
49 | CHW PIPING & ACCESSORIES WORKS | PIBCV | PRESSURE INDEPENDENT TYPE CONTROL VALVES WITH ACTUATORS (PIBCV 24 AC/DC power, 0-10 V DC control ): Supply, installation Testing and Commissioning of Two-way pressure independent type control valve motorised modulating actuators with linear stroke of minimum 15 mm,The actuator shall have shut off capability of min. 4 bar rating, 24V AC/DC operated, 0-10 V control, 0(2)-10 V feedback to BMS. tempreature and pressure plugs. The design of the valve should be non-clog type.The valve to have full authority. | [12 empty] | 0 | 0
49.01 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 200 mm dia | [10 empty] | QRO | NOS | 297546 | 4500 | 0 | 0 | 0
49.02 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 150 mm dia | [10 empty] | QRO | NOS | 205127 | 2813 | 0 | 0 | 0
49.03 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 125 mm dia | [10 empty] | QRO | NOS | 159065 | 2344 | 0 | 0 | 0
49.04 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 100 mm dia | [10 empty] | QRO | NOS | 126534 | 1875 | 0 | 0 | 0
49.05 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 80 mm dia | [10 empty] | 3 | NOS | 92067 | 1500 | 276201 | 4500 | 280701 | bar: Q3 to Q5
49.06 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 65 mm dia | [10 empty] | 1 | NOS | 86484 | 1219 | 86484 | 1219 | 87703 | bar: Q4
49.07 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 50 mm dia | Q3: 1; Q5: 1; Q6: 1; Q9: 3; Q10: 3 | 9 | NOS | 70664 | 938 | 635976 | 8442 | 644418
49.08 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 40 mm dia |  |  | 3 | 1 | 2 | 3 | 2 |  | 5 | 1 | 17 | NOS | 52926 | 750 | 899742 | 12750 | 912492
49.09 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 32mm dia | 6 |  | 4 | 4 | 4 | 3 | 4 | 1 | 10 |  | 36 | NOS | 34017 | 480 | 1224612 | 17280 | 1241892
49.1 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 25 mm dia |  | 2 |  | 1 | 1 | 2 | 1 | 3 | 6 |  | 16 | NOS | 22096 | 375 | 353536 | 6000 | 359536
49.11 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 20 mm dia | 2 |  |  | 1 | 1 | 1 | 1 |  | 2 |  | 8 | NOS | 18254 | 375 | 146032 | 3000 | 149032
49.12 | CHW PIPING & ACCESSORIES WORKS | PIBCV | 15 mm dia | [10 empty] | QRO | NOS | 17829 | 281 | 0 | 0 | 0
50 | CHW PIPING & ACCESSORIES WORKS | CHW VALVES | CONTROL VALVES WITH ACTUATORS (CV) : Supply, installation Testing and Commissioning of two way globe type control valves with actuators to be installed de-coupler line as per Specification. The actuators shall be suitable to be installed in open atmosphere and supplied with IP 65 rated environment protection. 3000 LPM flow, 3 Bar body rated, 300kPa close off rating and Kv value should be 181 for modulating purpose. iron body, bronze trim, rising stem, plug-type disc, flanged ends, and renewable seat and disc. The price shall include the cost of insulation similar to CHW pipes. | Q10: 3 | 3 | NOS | 66091 | 4500 | 198273 | 13500 | 211773 | We have considerd 200mm Motorised Butterfly Valve
51 | CHW PIPING & ACCESSORIES WORKS | RUBBER BELLOW | Double Sphere Rubber Bellows: Supply, installation, testing & commissioning of 150mm dia with 1600 kPa working pressure as per Specification. | Q10: 4 | 4 | Nos | 16784 | 2813 | 67136 | 11252 | 78388
51.01 | CHW PIPING & ACCESSORIES WORKS | RUBBER BELLOW | Double Sphere Rubber Bellows: Supply, installation, testing & commissioning of 200mm dia with 1600 kPa working pressure as per Specification. | Q10: 16 | 16 | Nos | 22887 | 4500 | 366192 | 72000 | 438192
51.02 | CHW PIPING & ACCESSORIES WORKS | RUBBER BELLOW | Double Sphere Rubber Bellows: Supply, installation, testing & commissioning of 250mm dia with 1600 kPa working pressure as per Specification. | Q10: 8 | 8 | Nos | 30516 | 5625 | 244128 | 45000 | 289128
51.03 | CHW PIPING & ACCESSORIES WORKS | RUBBER BELLOW | Double Sphere Rubber Bellows: Supply, installation, testing & commissioning of 300mm dia with 1600 kPa working pressure as per Specification. | [10 empty] | QRO | Nos | 40053 | 7500 | 0 | 0 | 0
52 | CHW PIPING & ACCESSORIES WORKS | THERMOMETER | DIAL TYPE THERMOMETER: Supply, installation, testing and commissioning of Indicating-dial type Stainless steel Case & Stem; Sensing element with Bi-metal strip coiled, IP 65 Protection, Dial with Aluminium black graduation on white background, Pointer with Aluminium black coloured Slotted zero adjustable, Window with Sheet Glass and of length to suit installation, Neoprene Gasket material, Accuracy with Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range, Measuring range 0-50 deg C as per specification with O & U Siphone with needle isolation valve. The vendor shall consider 150mm dia, dial for thermometer. | 1 |  | 2 | 2 | 4 | 9 | 5 | 3 | 15 | 19 | 60 | Nos | 1806 | 250 | 108360 | 15000 | 123360
53 | CHW PIPING & ACCESSORIES WORKS | PRESSURE GAUGE | PRESSURE GAUGES : Supply, installation, testing and commissioning of Indicating-dial type pressure gauges of Dry type made of Stainless steel or cast aluminum case, Pressure-Element Assembly: Bourdon tube,glycrine filled, Pressure Connection : Brass, NPS 12mm dia bottom-outlet type, Dial: Satin-faced, non-reflective aluminum with permanently etched scale markings, Pointer: Red or other dark-color metal, Window: Glass, Accuracy: Grade A, plus or minus 1 percent of middle half, Stainless Steel U-Siphon or O Siphon ,pressure snubber, GI nipple with coupling and 15mm Brass body ball valve as per Specification. Note. Provide Nitrile rubber insulation covered with Polyshield coating for U-siphon and valve used on Chilled water piping.The vendor shall consider 150mm dia, dial for pressure gauge. | 1 |  | 2 | 2 | 4 | 9 | 5 | 3 | 15 | 28 | 69 | Nos | 2108 | 250 | 145452 | 17250 | 162702
54 | CHW PIPING & ACCESSORIES WORKS | TEST POINT | TEST POINTS: Supply and installation of Test points of 1600 kPa working pressure, 6-mm dia, Brass / Bronze body, non return ing complete with suitable size socket, Screw cover, pipe nipples/couplings, insulation etc for Pressure & temperature measurement at various locations as per Specification | 19 | 1 | 23 | 20 | 6 | 38 | 66 | 62 | 31 | 12 | 278 | Nos | 321 | 63 | 89238 | 17514 | 106752
55 | CHW PIPING & ACCESSORIES WORKS | AUTO AIR VENTS | AUTO AIR VENTS : Supply, installation, testing and commissioning of Auto Airvents designed to vent automatically with float principle; bronze body and nonferrous internal parts; 1600kPaworking pressure; 30 deg C operating temperature as per Tender technical Specification.The vendor shall consider the price for neccessary isolation valve for Auto airvent. | 2 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 2 | 6 | 48 | Nos | 3136 | 250 | 150528 | 12000 | 162528
56 | CHW PIPING & ACCESSORIES WORKS | WATER FLOW SWITCH | WATER FLOW SWITCHES: General Purpose Flow Switches to prove flow on liquid lines using water, ethylene glycol solutions, or other liquids compatible with brass and phosphor bronze parts with SPDT contact switch, activated by liquid flow through the pipe. The set point shall be adjustable. Weather tight enclosure (IP 55 or higher). Stainless steel Paddle segments shall be removable or trimmed as needed, 20mm MPT connection with matching fittings and weldable couplings. (Approved makes: Siemens, Belimo, Johnson controls, honeywell). Please include the cost of suitable cabling to chiller control panel, in GI flexible conduit. Please refer technical specifications for complete details and scope & quote accordingly. | Q10: 4 | 4 | Nos | 1672 | 250 | 6688 | 1000 | 7688
57 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | DRAIN PIPING : Supply, installation and Commissioning of UPVC rated for 6Kg/Sq cm , solvent, with 9mm thick Aluminium foil faced Nitrile rubber insulation to make drain connection and U-Trap as per Tender Specification. | [10 empty] | QRO | Nos | 0 | 0 | 0 | 0 | 0
57.01 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 50 mm dia | [10 empty] | QRO | METER | 563 | 188 | 0 | 0 | 0
57.02 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 40 mm dia | [10 empty] | QRO | METER | 423 | 150 | 0 | 0 | 0
57.03 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 32 mm dia |  |  | 10 | 10 | 10 | 80 | 40 | 40 | 50 | 20 | 260 | METER | 354 | 124 | 92040 | 32240 | 124280
57.04 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 25 mm dia | 125 | 10 | 200 | 190 | 150 | 450 | 500 | 500 | 160 | 10 | 2295 | METER | 276 | 94 | 633420 | 215730 | 849150
58 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | PRESSURE PIPING : Supply, installation and Commissioning of CPVC pipe Schedule 40 complying to ASTM 441 high pressure pipe Schedule 40 , solvent connection, with 9mm thick Aluminium foil faced Nitrile rubber insulation to transfer condesnte water to roof with necessary valves and fittings as required as per Tender Specification and drawings. | [10 empty] | QRO | Nos | 0 | 0 | 0 | 0 | 0
58.01 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 100 mm dia | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 400 | METER | 2758 | 375 | 1103200 | 150000 | 1253200
58.01 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 80 mm dia | Q9: 60; Q10: 60 | 120 | METER | 1703 | 300 | 204360 | 36000 | 240360
58.02 | CHW PIPING & ACCESSORIES WORKS | DRAIN PIPING | 65 mm dia | Q10: 50 | 50 | METER | 1275 | 244 | 63750 | 12200 | 75950
59 | CHW PIPING & ACCESSORIES WORKS | AIR SEPARATOR | AIR & DIRT SEPARATOR : Supply, installation, testing and commissioning of microbubble Air & Dirt separator with 1600kPaworking pressure, 250 mm inlet and outlet pipe dia, fabricated steel body, flanged, air vent arrangement, 212 m3/hr flow rate, with air separator efficiency of 95%. | [10 empty] | 1 | Nos | 169461 | 18750 | 169461 | 18750 | 188211 | bar: Q10
60 | CHW PIPING & ACCESSORIES WORKS | OPEN EXPANSION TANK | CHILLED WATER EXPANSION TANK : Supply, Installation, Testing and Commissioning of 500 Litres Capacity PVC Tank (Sintex or equiv.) insulated with 25 mm thick nitrile rubber insulation, covered with 26G Aluminium Cladding including all accessories like Overflow, Drain valve, make-up Float valve, Air Vent arrangement etc | [10 empty] | QRO | Nos | 17561 | 9375 | 0 | 0 | 0
61 | CHW PIPING & ACCESSORIES WORKS | PRESSURIZATION UNIT AND CLOSED EXPANSION TANK | CHILLED WATER PRESSURIZATION UNIT & CLOSED EXPANSION TANK : Supply, installation, testing and commissioning of Closed bladder type expansion tank, 1600 Litres capacity minimum to meet system requirements, complete with 25 mm thick closed cell nitrile rubber with Al.cladding. The price shall include the cost of pressurization pumps (with one standby), starter panels, complete valve package mounted in a skid. The tank shall be mounted on Stand. | [10 empty] | 1 | Nos | 1107129 | 30000 | 1107129 | 30000 | 1137129 | bar: Q10
62 | CHW-EQUIPMENT | POT STRAINER | POT STRAINER: Supply, installation, testing & commissioning of 250 mm dia with 1000 kPa working pressure; Wire mesh shall be stainless steel 304. The complete valve assembly shall be insulated with similar insulation of chilled water piping as per Specification. | [10 empty] | 1 | Nos | 58298 | 6250 | 58298 | 6250 | 64548 | bar: Q10
63 | CHW PIPING & ACCESSORIES WORKS | CONDENSATE DISPOSAL | Design, fabrication, installation, testing and commissioning of factory fabricated condensate Triple layered insulated PVC tank with one number of submersible pump (ss casing) and internal SS piping, lifting arrangement, overflow pipe connections, drain valve connection, level transmitters and inbuilt control panel , skid mounting etc to complete the system. The system shall have level sensor and suitable controls to automatically switch ON / OFF the pump. The tank shall be insulated with 50 mm thick PUF panel and cladded with 26G Aluminium. The system shall be designed to store atleast 400 liter of water and able to handle a minimum flowrate of 10 CMH at 35m head. | Q1: 1; Q2: 2 | 3 | Nos | 81250 | 12500 | 243750 | 37500 | 281250
64 | CHW-EQUIPMENT | AUTOMATIC CHEMICAL DOZING | Supply, Installation,Testing & Commissioning & Handing over of the following for Automatic Chemical Dozing system: pH Control System, Acid Dosing with following components of 01 no. eachpH Sensor, Make: Ion Exchange / Equivalent, range: 0-14, output: mV, Body MOC: PVCpH Transmitter, Make: Ion Exchange / EquivalentMetering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP / Teflon Liquidend, with accessories like foot valve, strainer, injection valve, antisyphon valve.LDPE Tubing from Dosing Pump to Sampling Line Dosing Point.ORP Control System, Hypo Dosing with following components of 01 no. eachORP Sensor, Make: Ion Exchange / Equivalent, range: -1600-1600mV, output: mV, Body MOC: PVCORP Transmitter ; Make: Ion Exchange / EquivalentMetering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP Liquidend, with accessories like foot valve, strainer, injection valve etcPE Storage Tank, 60lts, lid with facility to mount the metering pumpLDPE Tubing from Dosing Pump to Sampling Line Dosing PointConductivity Control System with following components of 01 no. eacha. Conductivity Sensor ; Make: Ion Exchange / Equivalent Wetted materials – PVC b. Electrodes – SS c. Conductivity Transmitter, Make: Ion Exchange / Equivalent Blowdown Control Valve, 1” Size, Make: Ion Exchange/EquivalentAntiscalant Dosing System with following components of 01 no. each: Metering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP Liquidend, with accessories like foot valve, strainer, injection valve, antisyphon valve. PE Storage Tank, 60lts, lid with facility to mount the metering pump LDPE Tubing from Dosing Pump to Sampling Line Dosing PointOne Oxydising & one Non – Oxidising Biocide Dosing System with following components of 01 no. each: total 2 nos Metering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP Liquidend, with accessories like foot valve, strainer, injection valve. PE Storage Tank, 60lts, lid with facility to mount the metering pump | Q10: 0 | QRO | Set | 1001700 | 18750 | 0 | 0 | 0
64.01 | CHW-EQUIPMENT | AUTOMATIC CHEMICAL DOZING | LDPE Tubing from Dosing Pump to Sampling Line Dosing PointBio-Dispersant Dosing System with following components of 01 no. each: Metering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP Liquidend, with accessories like foot valve, strainer, injection valve. PE Storage Tank, 60lts, lid with facility to mount the metering pump LDPE Tubing from Dosing Pump to Sampling Line Dosing PointCorrosion Inhibitor Dosing System with following components of 01 no. each: Metering Pumps, Make: Ion Exchange/Equivalent, Max. Flow: 4LPH, Max. Injection Pressure: 4.0 kg/cm2 , PP Liquidend, with accessories like foot valve, strainer, injection valve. PE Storage Tank, 60lts, lid with facility to mount the metering pump LDPE Tubing from Dosing Pump to Sampling Line Dosing PointControl Panel comprising of *7’ Color display with Touch input for user-friendly Navigation *Continuous monitoring and proportional control for ph, orp and conductivity variables *Special inhibitor and dispersant dosing features *Flexible non ox biocide dosing program *Remote Access via secure website - No software installation or upgrades required *Alarms & events sent via SMS and/or e-mail *Online dashboard with Graphs and Plots *24 x 7 remote monitoring from centralized expert team *Green Technology benefits for Green Building certification Control Skid To house the above mentioned items along with required piping and internal cabling | [12 empty] | 0 | 0
65 | CHW-EQUIPMENT | IONIZATION WATER TREATMENT SYSTEM | Supply, installation, Testing & Commisioning of Electrolytic scale treatment system with components mounted on a skid 1. Reaction Tank 2. Electrodes 3. Scrapper (see the Inset picture) 4. Scrapper Motor 5. Control Panel Modbus connectivity 6. Inlet Connection 7. Inlet Valve 8. Outlet Connection 9. Outlet Valve 10. Drain Outlet 11. Drain Valve 12. Air Release/Intake Valve 13. Sediment FIltration with autoback wash.14. Pumping arrangement with necesaary valves strainer, nrv etc. and piping to complete the system. The mentioned are as bare minimum. Flow rate should be higher than the makeup water requirement or 10 % condenser flow rate whichever is higher. The system should be designed to meet the water paramenter as stated by Chiller condenser manufacturer recommendation. The system should be such so that the condenser water flow rate can be maintained at 15 COC or higher. The system should be designed with piping from to and from cooling tower basin. The system should be provided with performance guarantee | [10 empty] | 1 | Set | 2706250 | 312500 | 2706250 | 312500 | 3018750 | bar: Q10
66 | CHW PIPING & ACCESSORIES WORKS | MANUAL CHEMICAL DOZING & FLUSHING | Supply and execute, Condenser & Chilled Water Flushing, Chemical cleaning & Passivation with one time chemical dosing for chilled water system with Pot Dosing Arragement with required valves & piping to be done. The system pumps not be used for flushing activities. All arrangement for connection makeup & discharge to be arranged by the supplier. | [10 empty] | 1 | Set | 222750 | 187500 | 222750 | 187500 | 410250 | bar: Q10
67 | CHW-EQUIPMENT | STP WATER SOFTNER | Supply, Installation, testing and commissioning of Water Treatment System for STP Water to be treated with Water Softener plant with its required pumps, vales, piping, etc. for Feeding to Cooling Tower design based on Chiller Manufacturer recommendation to be desinged based on Make up water requirement for Chilled water system. | [10 empty] | 1 | Set | 567000 | 93750 | 567000 | 93750 | 660750 | bar: Q10
68 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT GI | FACTORY MADE GI RECTANGULAR DUCT : Supply, Erection, Installation, Testing and Commissioning of factory made rectangular ducts made out of 120 GSM galvanized steel sheet, complying to IS 277, SMACNA duct construction standard or or IS 655, pittsburgh seam lock profile with leak proof locking arrangement for longitudinal joints, duct fittings such as elbows, reducers, Y-piece, shoepiece etc., TDF flanges with its accessories upto 1500 mm ducts and MS angle flanges painted with red oxide primer and black color top coat above 1500 mm ducts, duct stiffener rods shall be provided above 750 mm ducts, guide vanes in elbow fittings shall be provided as per approved shop drawings, flanges shall be factory drilled for bolts i.e 4 bolt system for TDF and slotted holes for MS angles, low VOC water based sealant to arrest air leaks, duct bottom supports with GI slotted angles upto 750 mm and MS C-channel/L angle above 750 mm, wire rope hangers with looped end and rope lock, zinc coated GI threaded rods of different diameters as per duct sizes (minimum 8 mm rod), industrial grade anchor bolts of different diameters as per duct sizes, high tensile electroplated hexagonal bolts, nuts, carriage bolts and washers, 5 mm thick neoprene rubber gasket with all necessary supports and accessories. duct identification tags and air flow direction arrows labelling shall be provided as per approved shop drawing. duct bottom supports shall be provided at every 2400 mm length and wherever required as per site condition. duct mode of measurement shall be based on surface area. | [12 empty] | 0 | 0
68.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT GI | 18 G | [10 empty] | QRO | Sq.m | 2192 | 350 | 0 | 0 | 0
68.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT GI | 20 G | Q2: 40; Q3: 65; Q4: 95; Q5: 95; Q10: 220 | 515 | Sq.m | 1936 | 350 | 997040 | 180250 | 1177290
68.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT GI | 22 G |  | 30 | 350 | 365 | 410 | 70 |  |  | 90 | 200 | 1515 | Sq.m | 1268 | 313 | 1921020 | 474195 | 2395215
68.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT GI | 24 G | 470 | 40 | 1000 | 1300 | 1300 | 1350 | 1660 | 1725 | 1650 |  | 10495 | Sq.m | 1071 | 313 | 11240145 | 3284935 | 14525080
69 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT AL | FACTORY MADE AL RECTANGULAR DUCT : Supply, Erection, Installation, Testing and Commissioning of factory made rectangular ducts made out of 120 GSM galvanized steel sheet, complying to IS 737, SMACNA duct construction standard or IS 655, pittsburgh seam lock profile with leak proof locking arrangement for longitudinal joints, duct fittings such as elbows, reducers, Y-piece, shoepiece etc., TDF flanges with its accessories upto 1500 mm ducts and MS angle flanges painted with red oxide primer and black color top coat above 1500 mm ducts, duct stiffener rods shall be provided above 750 mm ducts, guide vanes in elbow fittings shall be provided as per approved shop drawings, flanges shall be factory drilled for bolts i.e 4 bolt system for TDF and slotted holes for MS angles, low VOC water based sealant to arrest air leaks, duct bottom supports with GI slotted angles upto 750 mm and MS C-channel/L angle above 750 mm, wire rope hangers with looped end and rope lock, zinc coated GI threaded rods of different diameters as per duct sizes (minimum 8 mm rod), industrial grade anchor bolts of different diameters as per duct sizes, high tensile electroplated hexagonal bolts, nuts, carriage bolts and washers, 5 mm thick neoprene rubber gasket with all necessary supports and accessories. duct identification tags and air flow direction arrows labelling shall be provided as per approved shop drawing. duct bottom supports shall be provided at every 2400 mm length and wherever required as per site condition. duct mode of measurement shall be based on surface area. | [12 empty] | 0 | 0
69.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT AL | 18 G | [10 empty] | QRO | Sq.m | 2370 | 350 | 0 | 0 | 0
69.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT AL | 20 G | [10 empty] | QRO | Sq.m | 2129 | 350 | 0 | 0 | 0
69.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT AL | 22 G | Q1: 15; Q4: 35; Q7: 70; Q9: 535; Q10: 260 | 915 | Sq.m | 1485 | 313 | 1358775 | 286395 | 1645170
69.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR DUCT AL | 24 G | [10 empty] | QRO | Sq.m | 1205 | 313 | 0 | 0 | 0
70 | AIR DISTRIBUTION AND LOWSIDE WORKS | MS DUCT | MS INSULATED DUCT FOR KITCHEN EXHAUST: Supply installation testing and commissioning of 16G MS Ducting with welded joints (grease tight) and access openings at the elbows. The Duct shall be fabricated and assembled at factory as per SMACNA standard for Class-500pascals. The ducts shall be fully welded construction with welded angle iron flanges and full faced gaskets. Gaskets shall be fire rated, non-porous, impervious to grease and cooking oils and capable of withstanding the higher temperatures experienced in kitchen extract systems in accordance with the approved shop drawings complete with all accessories like vanes, flanges, suspension rods, anchor bolts.Rockwool insulation of 75mm thick 120 Kg/m3 foil faced slab wrap around with metal strips, wiremesh and necessary pins to hold it in place for intended operation and tempreature rating. Necessary trap doors for duct cleaning shall be provided at elbows as per SMACNA. 2 coats of primer shall be provided to avoid rusting.The quoted price shall include the cost of minor works like wall opening & closing to run the supply & return ducts. The Pressure testing of sheet metal ducts shall be carried out for complete air distribution system, The testing shall be performed before insulating the ducts as per SMACNA standards. The entire air distribution system shall be balanced to supply the air quantities as required in various zones and rooms to maintain the specified room conditions. Air Balancing of each individual supply air outlet to within +10% or -5% of the design air quantity and tabulating the same in a form of report and also the final air balancing figures shall be indicated against each measured outlets in the as built drawings. Balancing shall also include balancing of return air, supply air and outdoor fresh air quantity. Calibrated air flow hoods shall be used for measuring the air flow across the square diffusers, Grill etc. and Calibrated velocity matric shall be used for measuring return air and calibrated pitot tubes with electronic controller to measure main duct airflow and static pressure. The vendor shall include the cost for pressure testing and air balancing. | Q5: 100; Q10: 50 | 150 | Sq.m | 3782 | 438 | 567300 | 65700 | 633000
71 | AIR DISTRIBUTION AND LOWSIDE WORKS | PRE-INSULATED DUCT | Supply of Pre-Insulated Ducting (Factory Pre-Cut) made of 20 mm thick PIR (Poly-Isocyanurate Rigid) Panels with 80-80 micron embossed aluminium Foli on both the side (Anti microbial, Anti fungal, Anti Dust & UV protected) on the both the sides with standard Accessories in Aluminum. PI Duct to be used for low pressure duct system e.g. FCUs only. |  |  | 75 | 85 | 130 | 100 | 50 | 50 | 50 | 50 | 590 | Sq.m | 1390 | 250 | 820100 | 147500 | 967600
72 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM | AHU PLENUMS : Supply, installation, testing and commissioning of factory fabricated 25-mm thick PUF filled double skin Supply air plenum with extruded GI profiles. The thickness of outer & inner skin GI sheet shall be 0.8 mm.. The plenum shall be fabricated only after consultants approval, as per site conditions and assembled at site, with factory cut opening for supply air ducts. | Q3: 20; Q4: 20; Q5: 20 | 60 | Sq.m | 5618 | 875 | 337080 | 52500 | 389580
73 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | GRILLES: Supply, installation, testing and commissioning of powder coated galvanized grilles as per specification. The color & pattern shall be pre-approved by Architects | 2 |  | 3 | 2 | 2 | 7 | 10 | 10 | 5 | 3 | 44 | Sq.m | 6199 | 1250 | 272756 | 55000 | 327756
74 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | COLLAR DAMPERS: Supply, installation, testing of duct mounted MS powder coated collar dampers. | 1 |  | 2 | 1 | 1 | 4 | 5 | 5 | 3 | 2 | 24 | Sq.m | 6019 | 1250 | 144456 | 30000 | 174456
75 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | AIR DIFFUSER : Supply and fixing of powder coated aluminium extruded 4-WAY, supply air flesh or stepped type diffuser (as per grid tile) with removable core as per specification. The color & pattern shall be pre-approved by Architects. The neck sizes are as follows. | [12 empty] | 0 | 0
75.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 225x225 (Neck size) overall size 595x595 | 46 |  | 136 | 70 | 54 | 4 | 32 | 22 | 54 | 64 | 482 | Nos | 1826 | 375 | 880132 | 180750 | 1060882
75.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 300x300 (Neck size) overall size 595x595 | 10 |  | 86 | 88 | 126 | 66 | 38 | 14 | 60 |  | 488 | Nos | 1826 | 375 | 891088 | 183000 | 1074088
75.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 375x375 (Neck size) overall size 595x595 | [10 empty] | QRO | Nos | 2000 | 375 | 0 | 0 | 0
75.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 450x450(Neck size) overall size 595x595 | [10 empty] | QRO | Nos | 2207 | 375 | 0 | 0 | 0
75.05 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 525x525(Neck size) overall size 595x595 | [10 empty] | QRO | Nos | 2408 | 375 | 0 | 0 | 0
76 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | PLENUM BOXES FOR SQUARE DIFFUSER: Supply, Installation, Testing, and Commissioning of Sheet Metal Plenum boxes made out of 0.4 mm (26 G) sheet for connecting the diffuser outlet & flexible connection from the main duct complete . The quote price shall include the cost of insulation with 9 mm thick closed cell nitrile rubber internally. The outlet of the box size shall match with diffuser neck size.Height of the spill air box shall be 300mm. | [12 empty] | 0 | 0
76.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | 225x225 (Neck size) | 23 |  | 68 | 35 | 27 | 2 | 16 | 11 | 27 | 32 | 241 | Nos | 1799 | 500 | 433559 | 120500 | 554059
76.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | 300x300 (Neck size) | 5 |  | 43 | 44 | 63 | 33 | 19 | 7 | 30 |  | 244 | Nos | 2307 | 500 | 562908 | 122000 | 684908
76.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | 375x375 (Neck size) | [10 empty] | QRO | Nos | 0 | 0 | 0 | 0 | 0
76.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | 450x450 (Neck size) | [10 empty] | QRO | Nos | 0 | 0 | 0 | 0 | 0
76.05 | AIR DISTRIBUTION AND LOWSIDE WORKS | PLENUM BOXES | 525x525(Neck size) | [10 empty] | QRO | Nos | 0 | 0 | 0 | 0 | 0
77 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | ROUND DIFFUSER: Supply, installation, testing and commissioning of extruded aluminium powder coated Round diffuser. | [12 empty] | 0 | 0
77.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 450 mm dia | [12 empty] | 2408 | 375
77.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 400 mm dia | [10 empty] | QRO | Nos | 2140 | 375 | 0 | 0 | 0
77.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 350 mm dia | [10 empty] | QRO | Nos | 1886 | 375 | 0 | 0 | 0
77.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 300 mm dia | [10 empty] | QRO | Nos | 1705 | 375 | 0 | 0 | 0
77.05 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 250 mm dia | [10 empty] | QRO | Nos | 1371 | 375 | 0 | 0 | 0
77.06 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 200 mm dia | [10 empty] | QRO | Nos | 1886 | 375 | 0 | 0 | 0
78 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 4-SLOT DIFFUSERS(Supply): Supply, installation, testing and commissioning of aluminium powder coated 4 slot 20mm wide diffusers with hit-miss dampers | [10 empty] | QRO | Sq.m | 2207 | 1250 | 0 | 0 | 0 | considred in RMT
79 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 4-SLOT DIFFUSERS (Return): Design, Manufacture, Supply, Installation, Testing, and Commissioning of aluminium powder coated 4 slot 20mm wide diffusers | [10 empty] | QRO | Sq.m | 1939 | 1250 | 0 | 0 | 0 | considred in RMT
80 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 3-SLOT DIFFUSERS(Supply): Supply, installation, testing and commissioning of aluminium powder coated 3 slot 20mm wide diffusers with hit-miss dampers | [10 empty] | QRO | Sq.m | 1939 | 1250 | 0 | 0 | 0 | considred in RMT
81 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 3-SLOT DIFFUSERS (Return): Design, Manufacture, Supply, Installation, Testing, and Commissioning of aluminium powder coated 3 slot 20mm wide diffusers | [10 empty] | QRO | Sq.m | 1672 | 1250 | 0 | 0 | 0 | considred in RMT
82 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 2-SLOT DIFFUSERS(Supply): Supply, installation, testing and commissioning of aluminium powder coated 2 slot 20mm wide diffusers with hit-miss dampers | [10 empty] | QRO | Sq.m | 1672 | 1250 | 0 | 0 | 0 | considred in RMT
83 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR TERMINALS | 2-SLOT DIFFUSERS (Return): Design, Manufacture, Supply, Installation, Testing, and Commissioning of aluminium powder coated 2 slot 20mm wide diffusers | [10 empty] | QRO | Sq.m | 1404 | 1250 | 0 | 0 | 0
84 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATED FLEXIBLE DUCT | INSULATED FLEXIBLE DUCT : Supply, Installation, Testing and Commissioning of Inner core should be made of double lamination of polyester film permanently bonded to a coated spring steel wire helix. Blanket of glass insulation of R 4.2 (RSI - 0.76 m2K/W) having density of 24 Kg/m3 and thickness of 25 mm shall be wrapped over the inner core and covered with tear and abuse resistant outer jacket cum vapour barrier made of fiber glass reinforced double layer of metalized polyester film laminate., duct shall be selected to suit the air flow velocity and pressure, wire hanger straps with chain support fixed over the circumference of the duct, jubilee clamp fixing arrangement at ends to rigid ducts finished with 50 mm wide black polyester tape, zinc coated GI threaded rods of different diameters as per duct sizes, industrial grade anchor bolts of different diameters as per duct sizes, high tensile electroplated hexagonal bolts, nuts and washers with all necessary supports and accessories.. flexible duct maximum installation length is 1200 mm and the remaining shall be rigid metal duct. duct mode of measurement shall be based on running metres. | [12 empty] | 0 | 0
84.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATED FLEXIBLE DUCT | 250 mm dia | [10 empty] | QRO | Rmt | 344 | 125 | 0 | 0 | 0
84.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATED FLEXIBLE DUCT | 200 mm dia | [10 empty] | QRO | Rmt | 281 | 125 | 0 | 0 | 0
84.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATED FLEXIBLE DUCT | 150 mm dia | 5 |  | 45 | 45 | 65 | 35 | 16 | 15 | 30 |  | 256 | Rmt | 225 | 125 | 57600 | 32000 | 89600
84.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATED FLEXIBLE DUCT | 100 mm dia | 25 |  | 70 | 35 | 30 | 2 | 20 | 10 | 30 | 35 | 257 | Rmt | 175 | 125 | 44975 | 32125 | 77100
85 | AIR DISTRIBUTION AND LOWSIDE WORKS | ACOUSTIC INSULATION | ACOUSTIC INSULATION : Supply, Installation, Testing and Commissioning of acoustic insulation made out of Class-1 open cell elastomeric nitrile rubber, 15 mm thickness, 140-220 Kg/m3 density, complying to BS 476 part 7, UL 94, thermal conductivity of 0.047 W/m.K at 20 °C, fibre free and antimicrobial complying to ASTM G21 and ASTM 2180, EPA approved, No erosion at ari velocity 10,000 FPM , low VOC self adhesive, operating temperature range shall be -20 °C to 85 °C, joints sealed with 50 mm wide black glass cloth tape with all necessary supports ansd accessories. If insulation is not self adhesive type, seperate adhesives used shall be of similar make of nitrile rubber insulation. acoustic insulation shall be internally/externally lined to ducts as per approved shop drawing. insulation mode of measurement shall be based on surface area. | 35 | 10 | 85 | 145 | 145 | 80 | 90 | 90 | 80 |  | 760 | Sq.m | 1000 | 250 | 760000 | 190000 | 950000
86 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | DUCT THERMAL INSULATION : (EXPOSED DUCTS) Supply, installation, testing and commissioning of 35mm (25+9) TOTAL Thickness with max. 2 layers closed-cell nitrile rubber Thermal conductivity not more than 0.37 W/(m-K) @20 Deg C (Class-O) with parafab -glass cloth shall have their laps adhered with protective coating class -1 starbond. two finish coat of protective coating starbond 30-36 shall be applied to entire outer surface of parafab - glass fiber cloth . All adhesives to be used shall be green building complaint. The Adesives cost shall be included. | Q10: 400 | 400 | Sq.m | 1255 | 250 | 502000 | 100000 | 602000
87 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | DUCT THERMAL INSULATION : Supplying and fixing of external thermal insulation on indoor ducts with approved sample of 13 mm green colour factory laminated fibre glass cloth on closed cell nitrile rubber (Anti-Microbial) with density 40-60 Kg/ Cum, class 'O' .Thermal conductivity not more than 0.37 W/(m-K) @20 Deg C. All longitudnal and transverse joints shall be sealed with 50mm wide and 3mm thick Nitrile rubber tape .The cost shall be inclusive of Low VOC adhesive and should comply LEED requirement. | 380 | 40 | 1325 | 1650 | 1650 | 935 | 950 | 950 | 1300 | 350 | 9530 | Sq.m | 676 | 250 | 6442280 | 2382500 | 8824780
88 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | DUCT THERMAL INSULATION : Supplying and fixing of external thermal insulation on indoor ducts with approved sample of 09 mm Blue colour factory laminated fibre glass cloth on closed cell nitrile rubber (Anti-Microbial) with density 40-60 Kg/ Cum, class 'O' .Thermal conductivity not more than 0.37 W/(m-K) @20 Deg C. All longitudnal and transverse joints shall be sealed with 50mm wide and 3mm thick Nitrile rubber tape .The cost shall be inclusive of Low VOC adhesive and should comply LEED requirement. | 95 | 10 | 332 | 413 | 413 | 234 | 238 | 238 | 325 | 88 | 2386 | Sq.m | 584 | 250 | 1393424 | 596500 | 1989924
88 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | AHU ROOM WALL ACOUSTIC : Design, Manufacture, Supply, Installation, Testing, and Commissioning of 25 mm thickness of Pre-Insulated Hi density glass wool Duct Board (suitable for Acoustic). All Duct Board shall be with outer side Factory laminated reinforced aluminium & inner with Black glass cloth. The price shall include the cost of 26G GI supporting channel 600x600 grid, on which the insulation board shall be fixed. Adhesives to be used shall be green building complaint. The price shall be applicable for any rectification works required in existing AHUs wall insulation. The insulation shall be accommodate within 600x600 grid. | 15 |  | 100 | 155 | 200 | 390 | 205 | 175 | 225 |  | 1465 | Sq.m | 1214 | 438 | 1778510 | 641670 | 2420180
89 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | UNDERDECK THERMAL INSULATION : Supply, installation, testing and commissioning of 32 mm Thick closed-cell nitrile rubber with factory applied aluminium foil, as shown in approved design drawings. All adhesives to be used shall be green building complaint. | [10 empty] | QRO | Sq.m | 780 | 313 | 0 | 0 | 0
90 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | UNDERDECK INSULATION : Supply, installation, testing and commissioning of Expanded Polystyrene (EPS) 50mm thickness of Density 48kg/m3 and should have Thermal Conductivity 0.65 k.m2/w, Water absorption shall be not more than 6% as per EN 13403 standard. | [10 empty] | QRO | Sq.m | 769 | 313 | 0 | 0 | 0
91 | AIR DISTRIBUTION AND LOWSIDE WORKS | INSULATION | UNDERDECK INSULATION : Supply, installation, testing and commissioning of preinsulated PIR(PolyIsocyanurate) Panels FSK Reinforced Aluminium foil on one side and 80 micron embossed aluminium on other side and 50mm Thickness with close cell not less than 95% Rigid Cellular foam insulation of thickness as specified below and material shall be Class O as per BS 476 Part 6 & Part 7, with Density of 48kg/m3 and should have Thermal Conductivity 0.019 W/mK , Water absorption shall be not more than 0.03% as per EN 13403 standard. | Q9: 3500 | 3500 | Sq.m | 1700 | 313 | 5950000 | 1095500 | 7045500
92 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | VARIABLE AIR VOLUME BOX WITH CONTROLLER: Design, Manufacture, Supply, Installation, Testing, and Commissioning of Variable Air Volume boxes shall be Pressure Independent type,constructed of 22 G galvanised steel which should be able to withstand salt spray test;VAV boxes must be factory fitted, callibrated and tested; Consisting of a 32 bit microprocessor Modbus MS/TP DDC Controller, Damper Actuator, Multi Point pick-up inlet Air Flow Velocity Sensor, Differential Pressure Transmitter,Analog type platinum element temperature sensor & Step-down Transformer.The DDC controller & actuator should be integral type & the ddc controller should have a spare analog input point that could be used for an occupancy or Co2 sensor.The DDC controllers used in the VAV terminals shall have the capacity to get directly interfaced with Modbus Building Automation Systems.All VAV terminals with DDC controller must be single OEM. Note - VAV boxes with controls to be assembled at factory and calibarated at factory. Witness for calibaration from client/consultants to be planned. The boxes shall be supplied with all internal attenuation treatment and acoustical damped casing necessary to achieve the required noise criteria. Casing shall be 20 BG minimum fitted with a completely sealed, easily removable means of access to all internal Parts. Maximum allowable static pressure to the boxes for its satisfactory operation shall not exceed 0.20” WG. Digital direct Output temperature sensor comprising of high quality thermistor or platinum sensing element should be supplied with VAVs. It should be possible to mount the sensor on the bottom surface of the false ceiling tile. Sample shall be approved. The look of the sensor should be rectangular in shape as shown in our schedule drawings showing VAV box quantities. Projection of the sensor should not exceed 27 mm . Necessary cabling between UPS power socket to VAV transformer ( Apr.. 3 Mtr length) with should be considered under the scope of work. plug top with socket with Power Cord should also to be part of scope.The color & pattern shall be pre-approved by Architects. | [12 empty] | 0 | 0
92.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 100 mm DIA (0-391 CMH) | [10 empty] | QRO | Nos | 29818 | 4375 | 0 | 0 | 0
92.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 125 mm DIA (119-612 CMH) | [10 empty] | QRO | Nos | 32092 | 4375 | 0 | 0 | 0
92.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 150 mm DIA (170-884CMH) | 8 |  | 41 | 70 | 27 | 5 |  |  | 10 |  | 161 | Nos | 32600 | 4375 | 5248600 | 704375 | 5952975
92.04 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 175 mm DIA (238-1207 CMH) | [10 empty] | QRO | Nos | 33630 | 4375 | 0 | 0 | 0
92.05 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 200 mm DIA (315-1572 CMH) | Q1: 2; Q3: 2; Q4: 3; Q5: 10; Q6: 1 | 18 | Nos | 33630 | 4375 | 605340 | 78750 | 684090
92.06 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 250 mm DIA (493-2465CMH) | Q3: 1; Q5: 2; Q6: 2 | 5 | Nos | 36385 | 4375 | 181925 | 21875 | 203800
92.07 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 300 mm DIA (714-3570 CMH) | [10 empty] | QRO | Nos | 42902 | 4375 | 0 | 0 | 0
92.08 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 350 mm DIA (986-4930 CMH) | Q3: 1; Q4: 4 | 5 | Nos | 45175 | 4375 | 225875 | 21875 | 247750
92.09 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV | 400 mm DIA (1258-6290CMH) | Q3: 4 | 4 | Nos | 47595 | 4375 | 190380 | 17500 | 207880
93 | AIR DISTRIBUTION AND LOWSIDE WORKS | CVR | CONSTANT VOLUME REGULATOR Supply installattion testing and commissioning of Constant Volume Regulators,The casing of the regulator is made from galvanized metal sheet, incorporates a rolling rubber ring seals in both ends, avoiding in such a way to have to spot or screw in a horizontal assemblies, includes plastic type ABS, Made of stainless steel, with a PUR coating in all RAL colours. | [12 empty] | 0 | 0
93.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | CVR | (0-500 CMH) | [10 empty] | QRO | Nos | 20063 | 3750 | 0 | 0 | 0
93.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | CVR | (501-1600 CMH) | [10 empty] | QRO | Nos | 20063 | 3750 | 0 | 0 | 0
94 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV INTEGRATOR | VAV INTEGRATOR : Supply, Installation, Programming and Commissioning of suitable one or more VAV integrators with enclosure for all proposed VAVs. The integrator shall provide VAV information to external BMS through Modbus over IP. The Vendor shall ensure that integrator shall handle minimum 44 VAVs. | [10 empty] | 1 | Nos | 121713 | 6250 | 121713 | 6250 | 127963 | bar: Q8
95 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV LOOPING CABLE | VAV LOOPING CABLE : Supply, Installation, Termination and Commissioning of suitable looping cable between VAV & Integrator to VAV looping The cable shall be laid in GI Conduit. Cost of conduits, supports and accessories shall be considered by vendor. | 250 |  | 1250 | 2000 | 1000 | 200 |  |  | 250 |  | 4950 | METER | 438 | 125 | 2168100 | 618750 | 2786850
96 | AIR DISTRIBUTION AND LOWSIDE WORKS | VAV SENSORCABLE | VAV THERMOSTAT CABLE: Supply, Installation, Termination and commissioning of suitable communication cable as per VAV OEM between VAV to VAV Thermostat. Cost of GI conduits, all accessoriess and supports shall be considered by vendor. | 150 |  | 740 | 1160 | 590 | 120 |  |  | 150 |  | 2910 | METER | 250 | 100 | 727500 | 291000 | 1018500
97 | AIR DISTRIBUTION AND LOWSIDE WORKS | ATTENUATOR | SOUND ATTENUATOR: Supply and fixing of acoustic lining (Sound Attenuator) of supply / return air duct, plenum and return air path in AHU room with 25mm thick resin bonded glass wool having density of 32 kg/cu.m, with 25mmx25mm G.I section of 1.2mm thick, at 600mm center to center covered with reinforced plastic tissue paper and 0.5mm thick perforated aluminium sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins etc. The mode of measurement shall be surface area of sheet metal. |  |  | 10 | 15 | 15 | 10 | 10 | 10 | 30 |  | 100 | Sq.m | 5906 | 1875 | 590600 | 187500 | 778100
98 | AIR DISTRIBUTION AND LOWSIDE WORKS | ATTENUATOR | CROSS TALK ATTENUATOR: Supply installation, testing and commissioning of 400 X 400 X 1500 mm, L / Z type, Factory fabricated Cross talk attenuators of 0.8 mm thick GI sheet, with 9 mm thick open cell nitrile rubber. | 7 |  | 41 | 72 | 32 | 5 |  |  | 11 |  | 168 | Nos | 3750 | 625 | 630000 | 105000 | 735000
99 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE DAMPER | SMOKE AND FIRE DAMPERS (MOTORISED): Design, Manufacture, Supply, Installation, Testing, and Commissioning of Motorized Fire and smoke damper where 3V blades and outer frames shall be of 16G GSS construction, The Fire dampers shall be UL 555 & /or UL 555S rated and certified by UL. FM Global approved, All fire dampers shall be complete with factory fabricated and fitted duct sleeve, Fire damper rating shall comply with leakage Class-1 (3.77 l/s @ 995 Pa static); enclosure temperature of 74 C and damper shall be 90 Minutes fire rated. The damper construction should be with frame, blades, blade stops, seals, linkage, axles, transformer to convert 240 V AC to DC Voltage, extended sleeve of 400mm length to 450 mm as per site requirement& thickness of 20G with complete boxing, the damper shall have auxillary / momentary switch to provide NO/NC signals with Resettable link ( RRL), Damper position feedback switch complete in all respect as per specification and drawings etc.Necessary control and power cabling for fire damper actuator to be considered. | 3 |  | 5 | 8 | 8 | 15 | 10 | 10 | 15 |  | 74 | Sq.m | 27018 | 1875 | 1999332 | 138750 | 2138082
100 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE DAMPER ACTUATOR | FIRE DAMPER ON / OFF ACTUATOR : Direct mounting electric damper actuator with Non spring return action,230V AC power supply, operated by binary output from BMS / other AC equipment / ventilation fan, Enclosed screw terminal strip for wiring, control panel with test, reset, indication arrangements, suitable transformers, Self-centering clamp fixing arrangement, The actuator shall be suitable to operate in the temperature range of 0 C to 60 C and Relative Humidity range of 5 to 95% RH at the temperature range specified. ( UL approved actuator).Vendor shall select the actuator of suitable torque and quote accordingly. | 7 |  | 16 | 10 | 23 | 38 | 27 | 23 | 61 |  | 205 | Nos | 20709 | 1250 | 4245345 | 256250 | 4501595
101 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE DAMPER | FIRE DAMPERS (FUSIBLE LINK): Design, Manufacture, Supply, Installation, Testing, and Commissioning of fusible link fire damper where 3V blades and outer frames shall be of 16G GSS construction, The Fire dampers shall be UL 555 & /or UL 555S rated and certified by UL. All fire dampers shall be complete with factory fabricated and fitted duct sleeve, Fire damper rating shall comply with leakage Class-1 (3.77 l/s @ 995 Pa static); enclosure temperature of 74 C and damper shall be 90 Minutes fire rated. The damper construction should be with frame, blades, blade stops, seals, linkage, axles. | [10 empty] | QRO | Sq.m | 19487 | 1875 | 0 | 0 | 0
102 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE DAMPER CONTROL PANEL | FIRE DAMPER CONTROL PANEL : Design, Manufacture, Supply, Installation, Testing, and Commissioning of Fire damper control panel, the control panel shall be capable of operating dampers based on fire input from FAS panel for auto operation and fire damper shall have the provision for monitoring actuator status through BMS. The multiple fire damper actuator shall be connected and controlled through single control panel. The vendor shall provide the local display with reset option. Vendor shall ensure that the control panel shall be compatible for output voltage of 220V. Vendor shall consider Power cable of minimum 1.5 meter with plug top with socket.Vendor shall consider minimum 8 actuators. | [10 empty] | 8 | Nos | 3585 | 1000 | 28680 | 8000 | 36680 | bar: Q1; Q3 to Q9
103 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE DAMPER CONTROL CABLE | FIRE DAMPER CONTROL CABLE : Design, Manufacture, Supply, Installation, Testing, and Commissioning of power cable required for connecting the fire damper actuators to fire damper control panel. The Looping shall be done for SA & RA Fire Dampers with single control panel and single control module from fire alarm system. | 10 |  | 20 | 20 | 20 | 20 | 10 | 10 | 10 |  | 120 | METER | 134 | 25 | 16080 | 3000 | 19080
104 | AIR DISTRIBUTION AND LOWSIDE WORKS | FIRE RETARDANT FLEXIBLE CANVAS | FIRE RETARDANT FLEXIBLE CANVAS : Supply, Installation, Testing and Commissioning of fire retardant canvas made out of neoprene glass fabric, flame resistant complying to ASTM E-84, NFPA 701, BS 476, EN 532, fabric secured to galvanized steel sheet on either sides by a double lock with air tight seam, operating temperature range shall be -30 °C to 160 °C, GI flanges matching with equipment and duct, minimum 150 mm depth, canvas and flange assemby concealed in galvanized steel sheet enclosure with acoustic insulation similar to duct, plug screws, nuts, bolts and washers, operable zip in accessible location with all necessary supports and accessories. canvas mode of measurement shall be based on surface area. | 1 |  | 3 | 3 | 5 | 5 | 10 | 10 | 10 |  | 47 | Sq.m | 4681 | 375 | 220007 | 17625 | 237632
105 | AIR DISTRIBUTION AND LOWSIDE WORKS | DUCT ACCESS DOOR | DUCT ACCESS DOOR : Supply, Installation, Testing and Commissioning of rectangular duct access door made out of galvanized steel sheet 120 GSM, 22 G frame and 24 G door panel with polycarbonate transparent view glass, hinged type door with chain riveted to hold door when opened or removable type door with lock knobs, door panel insulated with nitrile rubber similar to duct insulation, duct minimum 2 nos of hinges for hinged door, L-handle for door, minimum 2 nos of door locking knobs, door locking with angle frame lined with gasket for leak proofing with all necessary supports and accessories. duct access doors shall be provided in ductwork for fire damper access and other duct maintenance and inspection work as per approved shop drawing. door mode of measurement shall be based on surface area. | 1 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 15 | Sq.m | 4013 | 625 | 60195 | 9375 | 69570
106 | AIR DISTRIBUTION AND LOWSIDE WORKS | RECTANGULAR MANUAL VCD | RECTANGULAR MANUAL VCD : Supply, Installation, Testing and Commissioning of rectangular manual volume control dampers made out of extruded aluminum profile, 18 G frame and 20 G opposed 3V aerofoil blades, 150 mm depth, frame and blades connected by nylon bushes for lower sizes and machined spindles for larger sizes, EPDM blade seal, concealed PVC gear driven external linkage lever connected to blade shaft, shafts shall have extended spindle and shall be suitable to mount electric actuators when required, rectangular flanges to connect duct with nuts, bolts and washers, lockable type blade operating lever with needle pointer, open and close percentages engraved with all necessary supports and accessories. VCD mode of measurement shall be based on cross-sectional area. | 7 | 2 | 7 | 6 | 6 | 10 | 10 | 10 | 5 |  | 63 | Sq.m | 13235 | 1250 | 833805 | 78750 | 912555
107 | AIR DISTRIBUTION AND LOWSIDE WORKS | VOLUME CONTROL DAMPER | MOTORISED VOLUME CONTROL DAMPERS: Design, Manufacture, Supply, Installation, Testing, and Commissioning of Factory fabricated Rectangular shape - GI Volume control dampers, 1.6-mm GI Steel Frame, 1.6-mm GI blades, 150-mm width, with required hardware and accessories. The damper shaft shall be suitable to be connected to on/off actuator. Stiffen damper blades for stability. Include locking device to hold single-blade dampers in a fixed position without vibration & engraved marking on position of damper, as per specifications. | Q1: 2; Q2: 2; Q8: 2 | 6 | Sq.m | 9757 | 1875 | 58542 | 11250 | 69792
108 | AIR DISTRIBUTION AND LOWSIDE WORKS | VOLUME CONTROL DAMPER ACTUATOR | MODULATING DAMPER ACTUATOR : Direct mounting electric damper actuator with spring return action,220V AC power supply, operated by binary output from BMS / other AC equipment / ventilation fan, Enclosed screw terminal strip for wiring, Self-centering clamp fixing arrangement, The actuator shall be suitable to operate in the temperature range of 0 C to 60 C and Relative Humidity range of 5 to 95% RH at the temperature range specified. (Please note that this item is related for motorized VCD only. The actuators required for fire dampers shall not be quoted here).Vendor shall consider necessary cables for the actuator. Vendor shall select the actuator of suitable torque and quote accordingly. | Q1: 2; Q2: 2; Q8: 2 | 6 | Nos | 14044 | 1000 | 84264 | 6000 | 90264
109 | AIR DISTRIBUTION AND LOWSIDE WORKS | BACK-DRAFT DAMPERS | BACK-DRAFT DAMPERS: Supply, installation, testing and commissioning of Factory fabricated Round / Rectangular shape - GI Volume control dampers, 1.4-mm GI Steel Frame, Multiple-blade, parallel action gravity balanced, with center-pivoted blades of maximum 75-mm width, with sealed edges, assembled in rattle-free manner with 90-degree stop, steel ball bearings, and axles; and as per specifications. | [10 empty] | 7 | Sq.m | 7905 | 1250 | 55335 | 8750 | 64085 | bar: Q3 to Q9
110 | AIR DISTRIBUTION AND LOWSIDE WORKS | ROUND BUTTERFLY DAMPER | ROUND BUTTERFLY DAMPER : Supply, Installation, Testing and Commissioning of round butterfly dampers made out of galvanized steel sheet, 18 G casing and 20 G blade mounted on shaft enclosed in sleeve, gasket at blade tips to prevent leakage, round flange connections to connect round duct with nuts and bolts or slip on type coupling joint with rivet or screw fixed, low VOC water based sealant to arrest air leaks, jubilee clamp to connect flexible duct, lockable type blade operating lever with needle pointer, open and close percentages with all necessary supports and accessories. | [12 empty] | 0 | 0
110.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | ROUND BUTTERFLY DAMPER | 200 mm dia | [10 empty] | QRO | Nos | 875 | 250 | 0 | 0 | 0
110.02 | AIR DISTRIBUTION AND LOWSIDE WORKS | ROUND BUTTERFLY DAMPER | 150 mm dia | 5 |  | 43 | 44 | 63 | 33 | 19 | 7 | 30 |  | 244 | Nos | 803 | 250 | 195932 | 61000 | 256932
110.03 | AIR DISTRIBUTION AND LOWSIDE WORKS | ROUND BUTTERFLY DAMPER | 100 mm dia | 23 |  | 68 | 35 | 27 | 2 | 16 | 11 | 27 | 32 | 241 | Nos | 669 | 250 | 161229 | 60250 | 221479
111 | AIR DISTRIBUTION AND LOWSIDE WORKS | DISC VALVES | DISC VALVES : Supply, Installation, Testing and Commissioning of disc valve made out of powder coated galvanized steel sheet disc valve, minimum 1 mm thick with adjustable disc for controlling air flow by rotating disc in clockwise and anticlockwise direction, disc fastened to zinc coated threaded rod, valve seat with gasket, mounting ring, concealed fixing by means of screw with all necessary supports and accessories. Note : RAL code of the disc valve shall be as per client/architect. | [12 empty] | 0 | 0
111.01 | AIR DISTRIBUTION AND LOWSIDE WORKS | DISC VALVES | 150 mm Dia | 11 |  | 50 | 61 | 56 | 111 | 150 | 150 | 79 |  | 668 | Nos | 903 | 250 | 603204 | 167000 | 770204
112 | AIR DISTRIBUTION AND LOWSIDE WORKS | NON VISION DOOR GRILL | NON VISION DOOR GRILL : Supply, Installation, Testing and Commissioning of Non vision door grills made out of powder coated extruded aluminum minimum 1.2 mm thick with minimum frame depth as per door size, 30 mm flange size, inclined aluminum blades at 60 degrees, minimum 50% free area, vertical supporting mullions if grill width exceeds 600 mm, concealed fixing by means of screw to frame with all necessary supports and accessories. Non vision door grill mode of measurement shall be based on cross-sectional area. Note : RAL code of the louver shall be as per client/architect. | [10 empty] | 7 | Sq.m | 6019 | 1250 | 42133 | 8750 | 50883 | bar: Q3 to Q9
113 | AIR DISTRIBUTION AND LOWSIDE WORKS | LOUVER WITH BIRD SCREEN | LOUVER WITH BIRD SCREEN : Supply, Installation, Testing and Commissioning of louvers made out of powder coated extruded aluminum minimum 1.2 mm thick with minimum frame depth 45 mm, 30 mm flange size, inclined aluminum blades at 45 degrees, minimum 50% free area, vertical supporting mullions if louver width exceeds 600 mm, aluminum wire diamond mesh fixed on the back side of louver, concealed fixing by means of screw to frame with all necessary supports and accessories. louver mode of measurement shall be based on cross-sectional area. Note : RAL code of the louver shall be as per client/architect. |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 |  | 8 | Sq.m | 7931 | 1000 | 63448 | 8000 | 71448
114 | AIR DISTRIBUTION AND LOWSIDE WORKS | AIR PURIFIER (PHI CELL) | AIR PURIFIER (PHI CELL): Design, Manufacture, Supply, Installation, Testing, and Commissioning of duct / plenum mountable odor removal equipment to purify the air and to remove duct contaminants by employing the concept of plasma air ionization, with UV bulb monitoring system and saftey interlock switch. Approved make & model : Activeteck Model induct 16000 ozone free / Oz-air | Q3: 2; Q4: 2; Q5: 2 | 6 | Nos | 149800 | 6250 | 898800 | 37500 | 936300
115 | AIR DISTRIBUTION AND LOWSIDE WORKS | DRAIN PUMP | CONDENSATE DRAIN PUMP : Supply, installation, testing and commissioning of condensate drain pump should be manufactured from rigid PVC with a 4 litre capacity tank. The quote price shall include 25mm dia. PVC pipe insulated with 9mm thick closed cell nitrile rubber (Class-O) interconnecting piping from unit to the nearest drain line (Maximum length of 45m), the vendor should include the necessary mounting arrangement for the pumps. ASPEN Pump. This line item shall be operated only for ductable units. Drain pumps for Hiwall units shall be quoted in Hiwall unit line item. | 1 |  | 6 | 1 | 1 | 1 | 1 | 1 | 1 |  | 13 | Nos | 6460 | 1000 | 83980 | 13000 | 96980
116 | TESTING AND COMMISSINING | IAQ TEST | IAQ TEST: The Vendor is responsible to conduct the IAQ test, After completion of construction and before occupancy conduct an indoor air quality testing in regular ventilation conditions. The testing should be done by a ISO/IEC 17025 accredited laboratory for their test methods. The following compounds should be tested. The neccessary tools and tackles required to conduct the test shall be included. The test to be conducted for entire floor. The vendor shall consider the testing charges before and after occupancy. Minimum of 10 samples shall be considered for each zone. INDOOR AIR QUALITY ASSESSMENT •PM 10 •PM2.5 •Ozone •TVOCs •Formaldehyde | [10 empty] | QRO | Lot | 0 | 0 | 0 | 0 | 0
117 | TESTING AND COMMISSINING | OT VALIDATION | OT VALIDATION TEST: The vendor is responsible to conduct the OT validation of the system as per NABH recommendation. The testing should be done by a Every 6 month as per ISO 5 clean room according to 14644-1 std. The following compounds should be tested. The neccessary tools and tackles required to conduct the test shall be included.The test to be conducted for each OT. The vendor shall consider the testing charges before and after occupancy •Temperature and Humidity check • Air particulate count •Air Change Rate Calculation •Air velocity at outlet of terminal filtration unit /filters •Pressure Differential levels of the OT with respect to ambient / adjoining areas •Validation of HEPA Filters by appropriate tests | [10 empty] | QRO | Nos | 125000 | 0 | 0 | 0 | 0
118 | TESTING AND COMMISSINING | BUILDING FLUSHOUT | BUILDING FLUSHOUT : The vendor shall consider the necessary cost for the building flush out as per LEED requriement. The necessary fans, ducts, flexible ducts, power cables and accessories to be considered and quoted. The necessary window/Facade/Glaze opening and civil works required to be included. The quote shall be per floor flushout. | [10 empty] | 8 | Lot | 18750 | 6250 | 150000 | 50000 | 200000
119 | TESTING AND COMMISSINING | WILD AIR | WILD AIR : The vendor shall consider the necessary cost for the buildingwild air by running the HVAC system once the power is available by starting all the euuipnents without balacing with necessary temporary connection and comissioning filters. The TAB activiites to be carried out after wild air. The cost related to this shall be considered to do this functional test. The test to be done once the building envelop is closed. | [10 empty] | QRO | Lot | 0 | 0 | 0 | 0 | 0
120 | TESTING AND COMMISSINING | FILTERS | COMMISIONING FILTERS : Supply of temporary comisioning filters. | [10 empty] | 1 | Lot | 4375 | 625 | 4375 | 625 | 5000
119 | TESTING AND COMMISSINING | PRESSURE TESTING | PRESSURE TESTING : Pressure Testing and Sealing of all duct joints, flanges & other openings to ensure minimum leakage in the duct work and air distribution system. SMACNA standards shall be followed. The quote shall be for per AHU zone entire air distribution system. | [10 empty] | 1 | Lot | 125000 | 12500 | 125000 | 12500 | 137500
120 | TESTING AND COMMISSINING | AIR BALANCING WORKS | AIR BALANCING WORKS : Air Balancing of supply/return/intake/exhaust air distribution system by balancing the dampers and measuring the air flow rate by using calibrated flow hoods to achieve the designed air flow from the air terminals as per approved shop drawings. Air balancing test reports shall be submitted to the client/consultant in detailed tabular format mentioning the designed and measured air flow rates to comply with AABC/ NEBB standard | [10 empty] | 1 | Lot | 0 | 106250 | 0 | 106250 | 106250
121 | TESTING AND COMMISSINING | WATER BALANCING WORKS | WATER BALANCING WORKS : Chiller Plant Hydronic Testing and Water Balancing the valves and measuring the water flow rate by using calibrated machine to acheive the designed flow as per approved shop drawings. Water balancing test reports shall be submitted to the client / consultant in detailed tabular format mentioning the designed and measured flow rates to comply with AABC/ NEBB standard | [10 empty] | 1 | Lot | 0 | 150000 | 0 | 150000 | 150000
122 | VENTILATION FAN | VENTILATION FAN | CABINET EXHAUST AIR FAN: Design, Supply, Installation, Testing and commissioning of factory made, Floor / ceiling double skin Cabinet unit (25-mm thick CFC free PUF panels with 0.6-mm thick inner & 0.8-mm outer skin), DIDW with IE3 motors, Vibration isolators, GI base frame, Aluminum structural frame work, Fire retardant flexible connection, Access door, filter and accessories including equipment tagging and as per technical specifications furnished in this section. Motor Efficiency of the fan shall be minimum 65%. | [12 empty] | 0 | 0
122.01 | VENTILATION FAN | VENTILATION FAN | 1650 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 49986 | 4375 | 49986 | 4375 | 54361 | bar: Q1
122.02 | VENTILATION FAN | VENTILATION FAN | 2500 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 54574 | 4375 | 109148 | 8750 | 117898 | bar: Q3; Q5
122.03 | VENTILATION FAN | VENTILATION FAN | 2800 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 56175 | 4375 | 56175 | 4375 | 60550 | bar: Q9
122.04 | VENTILATION FAN | VENTILATION FAN | 3000 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 56175 | 6250 | 56175 | 6250 | 62425 | bar: Q10
122.05 | VENTILATION FAN | VENTILATION FAN | 4500 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 71229 | 6250 | 71229 | 6250 | 77479 | bar: Q3
122.06 | VENTILATION FAN | VENTILATION FAN | 5500 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 78024 | 6250 | 78024 | 6250 | 84274 | bar: Q3
121.01 | VENTILATION FAN | VENTILATION FAN | 5700 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 78024 | 6250 | 78024 | 6250 | 84274 | bar: Q2
122.01 | VENTILATION FAN | VENTILATION FAN | 6500 CMH, 400 Pa ESP | [10 empty] | 3 | Nos | 87785 | 6250 | 263355 | 18750 | 282105 | bar: Q2; Q6; Q10
122.02 | VENTILATION FAN | VENTILATION FAN | 16000 CMH, 400 Pa ESP | Q3: 2 | 2 | Nos | 215209 | 10625 | 430418 | 21250 | 451668
122.03 | VENTILATION FAN | VENTILATION FAN | 10500 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 129936 | 10625 | 129936 | 10625 | 140561 | bar: Q6
122.05 | VENTILATION FAN | VENTILATION FAN | 13500 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 142567 | 10625 | 142567 | 10625 | 153192 | bar: Q5
122.06 | VENTILATION FAN | VENTILATION FAN | 17000 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 215209 | 10625 | 215209 | 10625 | 225834 | bar: Q2
123 | VENTILATION PANEL | VENTILATION FAN PANEL | CABINET EXHAUST AIR FAN PANEL: Supply, installation, testing and commissioning of suitable electrical starter panel to match the design air flow & external static pressure, fabricated of 16G sheet metal enclosure powder coated using seven tank process, color Siemens gray, ceiling hung type, opening door width not to exceed 600mm(for single door) all cable entries will be top, knockout for cables will be factory cut,selector switch and indication lamps for Auto/Manual/OFF status.The rating of electrical panel and components shall be suitable to selected Ventilation fan motors.The panel shall have IP 54 rating.The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) ON/OFF status, (3) Run status, (4) Trip Status. | [12 empty] | 0 | 0
123.01 | VENTILATION PANEL | VENTILATION FAN PANEL | 1650 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q1
123.02 | VENTILATION PANEL | VENTILATION FAN PANEL | 2500 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 19251 | 4375 | 38502 | 8750 | 47252 | bar: Q3; Q5
123.03 | VENTILATION PANEL | VENTILATION FAN PANEL | 2800 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q9
123.04 | VENTILATION PANEL | VENTILATION FAN PANEL | 3000 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q10
123.05 | VENTILATION PANEL | VENTILATION FAN PANEL | 4500 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q3
123.06 | VENTILATION PANEL | VENTILATION FAN PANEL | 5500 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q3
122.07 | VENTILATION PANEL | VENTILATION FAN PANEL | 5700 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q2
123.01 | VENTILATION PANEL | VENTILATION FAN PANEL | 6500 CMH, 400 Pa ESP | [10 empty] | 3 | Nos | 19251 | 4375 | 57753 | 13125 | 70878 | bar: Q2; Q6; Q10
123.02 | VENTILATION PANEL | VENTILATION FAN PANEL | 16000 CMH, 400 Pa ESP | Q3: 2 | 2 | Nos | 19251 | 4375 | 38502 | 8750 | 47252
123.03 | VENTILATION PANEL | VENTILATION FAN PANEL | 10500 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q6
123.05 | VENTILATION PANEL | VENTILATION FAN PANEL | 13500 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q5
123.06 | VENTILATION PANEL | VENTILATION FAN PANEL | 17000 CMH, 400 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q2
124 | VENTILATION FAN | VENTILATION FAN | CABINET FRESH AIR FAN: Design, Supply, Installation, Testing and commissioning of factory made, Floor / ceiling double skin Cabinet unit (25-mm thick CFC free PUF panels with 0.6-mm thick inner & 0.8-mm outer skin), DIDW with IE3 motors, Vibration isolators, GI base frame, Aluminum structural frame work, Fire retardant flexible connection, Access door, and accessories including equipment tagging and as per technical specifications furnished in this section. Motor Efficiency of the fan shall be minimum 65%. | [12 empty] | 0 | 0
124.01 | VENTILATION FAN | VENTILATION FAN | 10440 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 133461 | 10625 | 133461 | 10625 | 144086 | bar: Q5
125 | VENTILATION FAN | VENTILATION FAN PANEL | CABINET FRESH AIR FAN: Supply, installation, testing and commissioning of suitable electrical starter panel to match the design air flow & external static pressure, fabricated of 16G sheet metal enclosure powder coated using seven tank process, color Siemens gray, ceiling hung type, opening door width not to exceed 600mm(for single door) all cable entries will be top, knockout for cables will be factory cut,selector switch and indication lamps for Auto/Manual/OFF status.The rating of electrical panel and components shall be suitable to selected Ventilation fan motors.The panel shall have IP 54 rating.The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) ON/OFF status, (3) Run status, (4) Trip Status. | [12 empty] | 0 | 0
125.01 | VENTILATION FAN | VENTILATION FAN PANEL | 10440 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q5
125 | VENTILATION FAN | VENTILATION FAN | INLINE FRESH AIR FANS: Supply, Installation, testing and commissioning of factory-fabricated, assembled,tested, and finished, direct-driven circular fans with filter consisting of internally lined housing, wheel, fan shaft, bearings, motor, drive assembly, with joints between sections sealed. The mounting frame shall be Galvanized Steel frames of minimum 3-mm Thick with factory fabricated corner pieces. The contractor shall provide twin-fans if the height of unit does not suit to false-ceiling height. The noise level of unit shall not be more than 55 dB(A) from 1.0 meter.The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) Auto/ Manual / OFF status, (3) Run status, (4) Trip Status. | [12 empty] | 0 | 0
125.01 | VENTILATION FAN | VENTILATION FAN | 300 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 45901 | 4375 | 0 | 0 | 0
125.02 | VENTILATION FAN | VENTILATION FAN | 500 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 45901 | 4375 | 0 | 0 | 0
125.03 | VENTILATION FAN | VENTILATION FAN | 650 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 45901 | 4375 | 0 | 0 | 0
125.04 | VENTILATION FAN | VENTILATION FAN | 700 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 47519 | 4375 | 0 | 0 | 0
125.05 | VENTILATION FAN | VENTILATION FAN | 900 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 47519 | 4375 | 0 | 0 | 0
125.06 | VENTILATION FAN | VENTILATION FAN | 1600 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 52645 | 4375 | 0 | 0 | 0
126 | VENTILATION FAN | VENTILATION FAN | INLINE EXHAUST AIR FANS: Supply, Installation, testing and commissioning of factory-fabricated, assembled,tested, and finished, direct-driven circular fans consisting of internally lined housing, wheel, fan shaft, bearings, motor, drive assembly, with joints between sections sealed. The mounting frame shall be Galvanized Steel frames of minimum 3-mm Thick with factory fabricated corner pieces. The contractor shall provide twin-fans if the height of unit does not suit to false-ceiling height. The noise level of unit shall not be more than 55 dB(A) from 1.0 meter.The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) Auto/ Manual / OFF status, (3) Run status, (4) Trip Status. | [12 empty] | 0 | 0
126.01 | VENTILATION FAN | VENTILATION FAN | 300 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 35840 | 4375 | 0 | 0 | 0
126.02 | VENTILATION FAN | VENTILATION FAN | 500 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 35840 | 4375 | 0 | 0 | 0
126.03 | VENTILATION FAN | VENTILATION FAN | 650 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 35840 | 4375 | 0 | 0 | 0
126.04 | VENTILATION FAN | VENTILATION FAN | 700 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 35840 | 4375 | 0 | 0 | 0
126.05 | VENTILATION FAN | VENTILATION FAN | 850 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 45728 | 4375 | 0 | 0 | 0
126.06 | VENTILATION FAN | VENTILATION FAN | 1600 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 50646 | 4375 | 0 | 0 | 0
126.07 | VENTILATION FAN | VENTILATION FAN | 1200 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 49233 | 4375 | 0 | 0 | 0
126.08 | VENTILATION FAN | VENTILATION FAN | 1650 CMH, 200 Pa ESP | [10 empty] | QRO | Nos | 49233 | 4375 | 0 | 0 | 0
127 | VENTILATION FAN | VENTILATION FAN | LOW NOISE CIRCULAR INLINE FANS FOR EXHAUST AIR : Supply, Installation, Testing and Commissioning of factory-fabricated, assembled, tested and finished, direct-driven circular inline fans consisting of internal thermally and acoustically lined housing, wheel, fan shaft, bearings, high efficiency motor, drive assembly. The quoted price shall include the cost of supply, installation, testing and commissioning of suitable electrical starter panel to match the design air flow & external static pressure, fabricated of 16 G sheet metal enclosure powder coated using seven tank process, color siemens gray. The rating of electrical panel and components shall be suitable to selected Ventilation fan motors. Efficiency of the fan shall be minimum 65 %. The panel shall have IP 54 rating. The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto/Manual command, (2) Auto/Manual ON/OFF Status, (3) Run Status, (4) Trip Status. The necessary control/power cables, plug and MS conduits to be considered. The vendor shall consider the cost for fire interlock module for tripping the fan incase of fire. Fans shall comply LEED requirements. sound levels shall be less than 65 dBA at 3m distance. The fan shall be operated at interval basis as per design. | [12 empty] | 0 | 0
127.01 | VENTILATION FAN | VENTILATION FAN | 300 CMH, 200 Pa ESP |  |  | 2 | 1 | 3 | 1 | 2 | 2 | 6 |  | 17 | Nos | 35509 | 3125 | 603653 | 53125 | 656778
127.02 | VENTILATION FAN | VENTILATION FAN | 350 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 35509 | 3125 | 35509 | 3125 | 38634 | bar: Q9
127.02 | VENTILATION FAN | VENTILATION FAN | 500 CMH, 200 Pa ESP | 1 |  | 1 | 1 | 1 | 1 |  | 1 | 2 |  | 8 | Nos | 35509 | 3125 | 284072 | 25000 | 309072
127.03 | VENTILATION FAN | VENTILATION FAN | 600 CMH, 200 Pa ESP | Q6: 3 | 3 | Nos | 35509 | 3125 | 106527 | 9375 | 115902
127.04 | VENTILATION FAN | VENTILATION FAN | 700 CMH, 200 Pa ESP | Q3: 1; Q4: 1; Q7: 3; Q9: 1 | 6 | Nos | 35509 | 3125 | 213054 | 18750 | 231804
127.05 | VENTILATION FAN | VENTILATION FAN | 750 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 35509 | 3125 | 35509 | 3125 | 38634 | bar: Q6
127.05 | VENTILATION FAN | VENTILATION FAN | 800 CMH, 200 Pa ESP | Q5: 1; Q7: 2 | 3 | Nos | 32224 | 3125 | 96672 | 9375 | 106047
127.06 | VENTILATION FAN | VENTILATION FAN | 1600 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 50177 | 3125 | 100354 | 6250 | 106604 | bar: Q4; Q7
127.07 | VENTILATION FAN | VENTILATION FAN | 1200 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 48777 | 3125 | 97554 | 6250 | 103804 | bar: Q3; Q9
127.08 | VENTILATION FAN | VENTILATION FAN | 1500 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 50177 | 3125 | 100354 | 6250 | 106604 | bar: Q5; Q8
127.08 | VENTILATION FAN | VENTILATION FAN | 1800 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 50177 | 3125 | 50177 | 3125 | 53302 | bar: Q4
128 | VENTILATION FAN | VENTILATION FAN | WALL MOUNTED PROPELLER FAN: Supply, Installation, Testing and Commissioning of Belt Driven Propeller Fans of capacities as mentioned below; The material of baldes and gravity damper shall be of GI material and the hub shall be of steel with corrosive resistance coating. The electircal IE-3 efficiency motor shall be of 1-phase /3-phase (415V) only and specific power consumption of entire fan unit shall be less than 50 watts / (1600 m3/hr). The acceptable sound pressure level of fan operation shall not exceed 64 dBA from 1.0 meter distance. The quoted fan assembly shall have following features as minimum: 1) GI internal protective mesh 2) GI bottom panel with minimum 2 rainwater holes 3) Pre-tensioned V belt with plastic safety guard The price shall include the cost of supports, mounting accessories such as wall bracket, bolts, nut,etc. The vendor shall include the cost of all electrical cabling works till power source / isolation switches provided by within 2 metre of fan location. The unit shall be selected for free static operation and Low RPM, however, static pressure requirement of gravity damper shall be included. | [12 empty] | 0 | 0
128.01 | VENTILATION FAN | VENTILATION FAN | 300 CMH |  |  | 5 | 5 | 8 | 3 | 1 | 2 | 6 |  | 30 | Nos | 10042 | 1875 | 301260 | 56250 | 357510
129 | VENTILATION FAN | VENTILATION FAN | PLUG FAN WITH DRY SCRUBBER: (EXHAUST AIR) Supply, Installation, Testing & Commissioning of factory-fabricated, -assembled, -tested, and -finished, backward-curved plug fans with EC motor consisting of 25 mm thick double skin cabinet, backward-Curved wheels, Shafts, Pre-lubricated and Sealed Shaft Bearings, , Scroll Access Doors, Cleanout Door, Motor, Vibration isolators, provide rain guard for the motors etc. The fan total static efficiency shall be more than 65%.The fan motor shall be mounted away the inlet air stream. The units shall be complete with washable aluminium mesh, pre-filter cells comprising of ionizing wires & collection plates. The efficiency of the scrubber unit up to 95% as per NIOSH 5026 Oil Mist Test (National Institute for Occupational Safety and Health). The quoted price shall include the cost of supply, installation, testing and commissioning of suitably rated electrical starter panel (IP55 rated) outdoor moutable, fabricated of 1.4 mm (16 G) sheet metal enclosure powder coated using seven tank process, color Siemens gray, wall mounted type, opening door width not to exceed 600mm(for single door) all cable entries will be top, knockout for cables will be factory cut, selector switch and indication lamps for Auto/Manual/OFF status. The electrical panel shall have necessary relays, potential free contacts to be interlocked with fire alarm control module to trip the motor incase of fire.The entire unit shall be selected for noise pressure level of 75 dBA from 1.0 meter distance. | [12 empty] | 0 | 0
129.01 | VENTILATION FAN | VENTILATION FAN | 13050 CMH, 400pa ESP | [10 empty] | 1 | Nos | 1380000 | 18750 | 1380000 | 18750 | 1398750 | bar: Q10
130 | VENTILATION FAN | SISW FAN | SISW CENTRIFUGAL FAN (KITCHEN HOOD EXHAUST FAN): Supply, Installation, Testing & Commissioning of factory-fabricated, -assembled, tested, and finished, belt-driven centrifugal fans consisting of Housing, backward-Curved wheels, Shafts, Pre-lubricated and Sealed Shaft Bearings, Belt Drives, Scroll Access Doors, Cleanout Door, Motor, Vibration isolators, provide rain guard for the motors etc. The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) Auto/ Manual / OFF status, (3) Run status, (4) Trip Status. | [12 empty] | 0 | 0
130.01 | VENTILATION FAN | SISW FAN | 13050 CMH, 400pa ESP | [10 empty] | QRO | Nos | 139586 | 18750 | 0 | 0 | 0
131 | VENTILATION FAN | SMOKE EXTRACTION FANS | AXIAL FANS (SMOKE EXTRACT): Design ,Supply, installation, testing & commissioning of Direct driven Smoke Spill Axial flow fan with galvanized steel Double flanged long casing, impellers of pressure casted aluminum adjustable pitch blades (Hub and Aero foil blades). The entire assembly of fan shall be suitable to operate at fire mode condition to withstand the temperature of 250 deg C for Two hour , IP 54 protection with direct driven motor and the air flowing from impeller to the motor for Basement ventilation application as per specification. Motor shall be suitable for 415±10% Volts, 50 Hz, 3 phase AC supply. Each fan shall include all accessories, controls, Flexible connection, vibration isolators as given below: The noise level shall be 65 dBA at 3 m distance | [12 empty] | 0 | 18750
131.01 | VENTILATION FAN | SMOKE EXTRACTION FANS | 1600CMH, 150 Pa ESP | [10 empty] | 1 | Nos | 49244 | 4375 | 49244 | 4375 | 53619 | bar: Q1
131.02 | VENTILATION FAN | SMOKE EXTRACTION FANS | 3400 CMH, 200 Pa ESP | Q9: 2 | 2 | Nos | 51987 | 6250 | 103974 | 12500 | 116474
131.03 | VENTILATION FAN | SMOKE EXTRACTION FANS | 3800 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 51588 | 6250 | 103176 | 12500 | 115676 | bar: Q6 to Q7
131.04 | VENTILATION FAN | SMOKE EXTRACTION FANS | 4700 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 53027 | 6250 | 53027 | 6250 | 59277 | bar: Q7
131.05 | VENTILATION FAN | SMOKE EXTRACTION FANS | 5000 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 53027 | 6250 | 53027 | 6250 | 59277 | bar: Q7
131.06 | VENTILATION FAN | SMOKE EXTRACTION FANS | 7200 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 60688 | 9375 | 60688 | 9375 | 70063 | bar: Q7
131.07 | VENTILATION FAN | SMOKE EXTRACTION FANS | 7400 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 61282 | 9375 | 61282 | 9375 | 70657 | bar: Q8
131.08 | VENTILATION FAN | SMOKE EXTRACTION FANS | 7600 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 61282 | 9375 | 61282 | 9375 | 70657 | bar: Q8
131.02 | VENTILATION FAN | SMOKE EXTRACTION FANS | 9200 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 71631 | 9375 | 71631 | 9375 | 81006 | bar: Q8
131.05 | VENTILATION FAN | SMOKE EXTRACTION FANS | 12400 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 81476 | 10625 | 81476 | 10625 | 92101 | bar: Q8
131.06 | VENTILATION FAN | SMOKE EXTRACTION FANS | 10500 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 80639 | 10625 | 80639 | 10625 | 91264 | bar: Q9
131.07 | VENTILATION FAN | SMOKE EXTRACTION FANS | 13100 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 81476 | 12500 | 81476 | 12500 | 93976 | bar: Q6
131.08 | VENTILATION FAN | SMOKE EXTRACTION FANS | 13700 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 91925 | 12500 | 91925 | 12500 | 104425 | bar: Q7
131.03 | VENTILATION FAN | SMOKE EXTRACTION FANS | 14000CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 91925 | 12500 | 91925 | 12500 | 104425 | bar: Q1
132 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | AXIAL FANS (SMOKE EXTRACT): Supply, installation, testing and commissioning of suitable electrical starter panel to match the design air flow & external static pressure, fabricated of 16G sheet metal enclosure powder coated using seven tank process, color Siemens gray, ceiling hung type, opening door width not to exceed 600mm(for single door) all cable entries will be top, knockout for cables will be factory cut,selector switch and indication lamps for Auto/Manual/OFF status.The rating of electrical panel and components shall be suitable to selected Ventilation fan motors.The panel shall have IP 54 rating. The electrical starter panel shall have necessary relay and potential free contacts for the following BMS provisions : (1) Auto / Manual command, (2) Auto/ Manual / OFF status, (3) Run status, (4) Trip Stat | [12 empty] | 0 | 0
132.01 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 1600CMH, 150 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q1
132.02 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 3400 CMH, 200 Pa ESP | Q9: 2 | 2 | Nos | 19251 | 4375 | 38502 | 8750 | 47252
132.03 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 3800 CMH, 200 Pa ESP | [10 empty] | 2 | Nos | 19251 | 4375 | 38502 | 8750 | 47252 | bar: Q6 to Q7
132.04 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 4700 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q7
132.05 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 5000 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q7
132.06 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 7200 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q7
132.07 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 7400 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q8
132.08 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 7600 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q8
132.09 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 9200 CMH, 200 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q8
132.1 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 12400 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q8
132.11 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 10500 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q9
132.12 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 13100 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q6
132.13 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 13700 CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 8 | 19251 | 8 | 19259 | bar: Q7
132.14 | VENTILATION PANEL | SMOKE EXTRACTION FANS PANEL | 14000CMH, 250 Pa ESP | [10 empty] | 1 | Nos | 19251 | 4375 | 19251 | 4375 | 23626 | bar: Q1
133 | VENTILATION FAN | CAR PARK VENTILATION | CAR PARK VENTILATION: Dismantling, Lowering of Existing Jet/ Vent Fans, Store it in Safe place (at Site only) and again shifting, Lifting, Reinstalling in the Basement Floor as per latest basement ventilation layout etc., and Testing and Commissioning of the same if necessory Servicing of the Fan's to be carried out by the Successfull contractor for which contractor has to visit the site, survey / check the condition of Fan's and quote their price accordingly. Note:- HVAC Contractor should check / verify the condition of existing Jet/ Vent Fans and confirm whether the fan is in good condition or Not. If the Jet/ Vent Fan's are not in good condition quote for Supply Installation Testing and Commissioning of the same. | [12 empty] | 0 | 0
133.01 | VENTILATION FAN | CAR PARK VENTILATION | Dismantlling & Resintallation of existing Jet Fans. Any upkeep or maintenance required to be part of the quote. | Q1: 22; Q2: 18 | 40 | Nos | 0 | 18750 | 0 | 750000 | 750000
133.02 | VENTILATION FAN | CFD | CFD Analysis for Carpark ventialtion to confirm the capacity of the system and location of Jet Fans simulation, tempreature, smoke, velocity , visibility to comply to tenable condition during fire mode. | [10 empty] | 2 | Nos | 0 | 43750 | 0 | 87500 | 87500 | bar: Q1 to Q2
133.03 | VENTILATION FAN | CAR PARK VENTILATION | SITC of AMCA certified Smoke Spill TUBE AXIAL FAN in arrangement 4 shall be complete with 900mm long silencer at inlet with all G.I supports ,Silencer pressure drop shall not be exceed 3 mm Wg and silencer selection sheet to be submitted. Fan with TEFC high temp IE3 motor with impeller (Hub and blades) shall be constructed of die cast aluminum alloy. Impeller should have aerodynamic profile, Casing made of Galvanized steel. Direction of discharge and rotation position shall be as per the job requirement.Please refer technical specification for further data. The fan mounted on a foot mount / G.I frame for ceiling suspended, bird Screen, G.I Back draft damper, spring isolator and fixing bolts and nuts, fire rated canvass connection,spring isolators, G.I supports etc.. to complete the job as per tender specification. . Fan shall be tested and certified in accordance with EN12101-3:2015 for smoke application. Noise level of fan not more than 75 dBA @ 1.5 mtr distance and fan to be selected accordingly. (Fan velocity shall not exceed 11 m/s ) | [12 empty] | 0 | 0 | 0 | 0 | 0
133.04 | VENTILATION FAN | CAR PARK VENTILATION | 46000 CFM- STATIC PRESSURE 25 MM WG. - ZONE 02 – 1600Ø | Q2: 2 | 2 | Nos | 534346 | 25000 | 1068692 | 50000 | 1118692
133.05 | VENTILATION FAN | CAR PARK VENTILATION | 30000 CFM- STATIC PRESSURE 25 MM WG. - ZONE 01 – 1400Ø | Q1: 2 | 2 | Nos | 359948 | 25000 | 719896 | 50000 | 769896
133.06 | VENTILATION FAN | CAR PARK VENTILATION | 35500 CFM- STATIC PRESSURE 25 MM WG. - ZONE 02 – 1400Ø | Q1: 2 | 2 | Nos | 385550 | 25000 | 771100 | 50000 | 821100
133.07 | VENTILATION FAN | CAR PARK VENTILATION | SITC of AMCA certified Fresh Air TUBE AXIAL FAN in arrangement 4 shall be complete with 900mm long silencer at inlet with all G.I supports ,Silencer pressure drop shall not be exceed 3 mm Wg and silencer selection sheet to be submitted. Fan with TEFC high temp IE3 motor with impeller (Hub and blades) shall be constructed of die cast aluminum alloy. Impeller should have aerodynamic profile, Casing made of Galvanized steel. Direction of discharge and rotation position shall be as per the job requirement.Please refer technical specification for further data. The fan mounted on a foot mount / G.I frame for ceiling suspended, bird Screen, G.I Back draft damper, spring isolator and fixing bolts and nuts, fire rated canvass connection,spring isolators, G.I supports etc.. to complete the job as per tender specification. .. Noise level of fan not more than 75 dBA @ 1.5 mtr distance and fan to be selected accordingly. (Fan velocity shall not exceed 11 m/s ) | [12 empty] | 0 | 0 | 0 | 0 | 0
133.08 | VENTILATION FAN | CAR PARK VENTILATION | 30000 CFM- STATIC PRESSURE 25 MM WG. - ZONE 01 – 1400Ø | Q2: 2 | 2 | Nos | 359948 | 25000 | 719896 | 50000 | 769896
133.09 | VENTILATION FAN | CAR PARK VENTILATION | 35500 CFM- STATIC PRESSURE 25 MM WG. - ZONE 02 – 1600Ø | Q1: 2 | 2 | Nos | 385550 | 12500 | 771100 | 25000 | 796100
133.1 | VENTILATION FAN | CO SENSOR | SITC of Carbon Monoxide Detectors (Range 0 to 300ppm) min coverage area of each sensor to be 700 Sq.mts & Installation of CO Sensors in 22guage Stainless steel 316L Perforated Box along with necessary support & accessories (as per the specifications) | Q1: 10; Q2: 20 | 30 | Lot | 18458 | 1875 | 553740 | 56250 | 609990
133.11 | VENTILATION PANEL | ELECTRICAL PANEL | Assessment, Revamp, Dismantlling & Resintallation of existing Car park ventilation fan to meet the requirements to be part of the cost. Any replacement or modifcation required in the panel to be part of the scope. | [10 empty] | 2 | Nos. | 0 | 18750 | 0 | 37500 | 37500 | bar: Q1 to Q2
134 | CHW-EQUIPMENT | PLATE TYPE HEAT EXCHANGER | Supply, Installation, Testing and Commissioning of Plate Type Heat exchanger considering both sides as water. The plate and frame heat exchanger shall consist of SS-316 and plates with a minimum thickness of 0.5 mm. Each plate shall incorporate a tongue and groove interlock design with non-glued NBR gaskets.Use of epoxy or heat cured adhesives is not permitted. Gaskets shall have leak detection grooves vented to the atmosphere to prevent intermixing of fluids.Each circuit shall be hydro tested independently at 1.3 times the design pressure of the unit.Frame shall be bolted construction and frame design must allow for a minimum of 20% expansion. Tie bolts shall be zinc plated EN-18 alloy steel. Unit shall be PN-16 rated. Unit shall be complete in all respects for following parameter: | [12 empty] | 0 | 0
134.01 | CHW-EQUIPMENT | PLATE TYPE HEAT EXCHANGER | Plate Heat Exchanger of 45 kW capacity. Temperature profile for side 1: 8 C - 11.86 C Temperature profile for side 2: 12.86 C - 7 C Valves, piping and insulation as required | Q10: 2 | 2 | Nos | 0 | 0 | 0 | 0 | 0 | We have not quoted for this item due to lack of clarity
135 | VENTILATION FAN | BLDC FAN | CEILING MOUNTED BLDC FAN: Supply, Installation, Testing & Commissioning of factory-fabricated, -assembled, tested, and finished, BLDC fans consisting of Housing, wheels, Shafts, Motor, etc. | Q3: 10; Q4: 30; Q5: 40; Q6: 20 | 100 | Nos | 8625 | 375 | 862500 | 37500 | 900000
136 | TESTING AND COMMISSINING | AIRFLOW MEASUREMENT STATION | AIRFLOW MEASUREMENT STATION: Supply, installation, testing and commissioning of airflow measurement station, factory mounted pre piped in flanged duct section, galvanised casing, anodized aluminium flow sensor, single/multiple airflow element with in 2percent of actual airflow , K factor 0.09, velocity ranges from 100 to 16000 FPM. Process connection shall be compression fitting. The vendor shall consider MODBUS communication protocol for airflow station.The size of station shall be selected as per FA AHU capacity. | Q1: 1; Q5: 1; Q7: 2; Q9: 10 | 14 | Nos | 211618 | 31250 | 2962652 | 437500 | 3400152
137 | MISCELLANEOUS | AIR CURTAIN | AIR CURTAIN : Supply, Installation, Testing and Commissioning of hospital application air curtain made out of MS powder coated material, dynamically balanced down facing aluminum blowers, 20-24 m/s air discharge velocity, effective throw minimum 3.5 m, noise levels 50 - 60 dB @ 3m distance, limit switch for auto operation when door is open, power cables of 20 m length, plug top with socket with all necessary accessories and supports. Note : No.of air curtains required i.e one or more required for the below sizes shall be considered and quoted." | [12 empty] | 0 | 0
137.01 | MISCELLANEOUS | AIR CURTAIN | Suitable for 2150 mm (W) x 2400 (H) Door | Q3: 2 | 2 | Nos | 45152 | 5000 | 90304 | 10000 | 100304
137.02 | MISCELLANEOUS | AIR CURTAIN | Suitable for 2000 mm (W) x 2400 (H) Door | Q3: 3 | 3 | Nos | 43933 | 5000 | 131799 | 15000 | 146799
138 | ELECTRICAL | VFD | VARIABLE FREQUNECY DRIVES : Supply, Installation, testing & commissioning of HVAC dedicated VFDs suitable for the following motor capacity of IP 21 rating Built-in dual 5% impedance DC link reactor on the positive and negative rails of the DC bus of the VFD. Thdi not increase more than 35% Built-in EMC Filters (electromagnetic compatibility filters) for VFDs for restriction of conducted emissions to comply with IEC61800: 3 (unrestricted distribution): 2004 Category C1, for required length of cable between motor & VFD. Automatic Energy Optimization for maximum energy savings. PID (Proportional integrated derivative) controller having capability to input signals from temperature/pressure sensor (in form of 0-10V or 4-20mA) for process optimization and accordingly regulate the speed of the AHUs. - The VFD shall be compatible with BMS, communicate via Modbus protocol (in baud rate of 9.6kbps & higher) Should have Analog inputs (0-10V DC) to accept control signal from BMS for Modulation (Incase of Open loop control) Should have Digital Inputs to take to accept command from BMS to start/stop VFD operation Should have a Operator control terminal cum display for Manual operation & setting changes | [12 empty] | 0 | 0
134.02 | ELECTRICAL | VFD | 1.5 KW | [10 empty] | QRO | Sq.m | 56603 | 2500 | 0 | 0 | 0
134.03 | ELECTRICAL | VFD | 2.2 KW | [10 empty] | QRO | Sq.m | 67972 | 2500 | 0 | 0 | 0
136.01 | ELECTRICAL | VFD | 2.5 KW | [10 empty] | QRO | Sq.m | 94963 | 2500 | 0 | 0 | 0
136.02 | ELECTRICAL | VFD | 3.7 KW | [10 empty] | QRO | Sq.m | 77522 | 2500 | 0 | 0 | 0
137.02 | ELECTRICAL | VFD | 5.5 kW | Q10: 8 | 8 | Sq.m | 89265 | 2500 | 714120 | 20000 | 734120
134.04 | ELECTRICAL | VFD | 7.5 kW | Q10: 2 | 2 | Sq.m | 100099 | 2500 | 200198 | 5000 | 205198
137.01 | ELECTRICAL | VFD | 9.3 kW | [10 empty] | QRO | Sq.m | 131777 | 2500 | 0 | 0 | 0
137.02 | ELECTRICAL | VFD | 11 kW | Q10: 4 | 4 | Sq.m | 131777 | 2500 | 527108 | 10000 | 537108
137.03 | ELECTRICAL | VFD | 15 kW | Q10: 4 | 4 | Sq.m | 149078 | 2500 | 596312 | 10000 | 606312
138.01 | ELECTRICAL | VFD | 18.5 KW | Q10: 2 | 2 | Sq.m | 185103 | 2500 | 370206 | 5000 | 375206
138.02 | ELECTRICAL | VFD | 22 KW | Q10: 2 | 2 | Sq.m | 215739 | 2500 | 431478 | 5000 | 436478
139 | MISCELLANEOUS | PEB SHEET OPENING AND CLOSING FOR HVAC EQUIPMENTS | PEB SHEET OPENING AND CLOSING FOR HVAC EQUIPMENTS : PEB sheet opening, closing, debris clearance and disposal for installing wall mounted fans, passing HVAC ducts, installing wall louvers and other HVAC works as per approved shop drawings. sheet openings shall be done after approval from engineer-in-charge. sheet openings shall by done by metal cutting machines keeping allowable tolerance for equipments as per approved shop drawings. sheet closing shall be done after installing the HVAC equipments with waterproof and air tight fire sealant. The PEB sheet opening and closing work shall be certified by the engineer-in-charge. mode of measurement shall be surface area of the PEB sheet. | [10 empty] | QRO | Sq.m | 0 | 0 | 0 | 0 | 0
140 | MISCELLANEOUS | PLANT ROOM ENCLOSURE | PLANT ROOM ENCLOSURE : Supply & Installation Acoustic Room enclosure with its own supporting strucuture duly painted as specified elsewhere in the BOQ for Chiller Plant Room to be made out of CSCA Or Pre –Galvanized Mild Sheet Steel prefabricated sheets with 50mm thick rockwool insulation or prefabricated PUF Panels with strucutral insulation panels, must be able to with stand local climate conditions, must accommodate for ventilation as required by indoor equipment, enclosure must be able to achieve 55 Dba @ 3 Mtr. The enclosure should be designed in such a way to enable for maintenance activity an must be corrosion proof and to allow for drainage. | [10 empty] | 1000 | Sq.m | 4200 | 1250 | 4200000 | 1250000 | 5450000
140 | MISCELLANEOUS | MILD STEEL SUPPORT | MILD STEEL SUPPORT WORKS : Supply, Fabrication, Finishing, Painting and Installation of mild steel support for constructing equipment platforms, ramps, staircases, stands, frames, pipe & duct supports and as required as per site condition, complying to ISA, ISMC, ISMB in the form of L-angles, C-channels, struts, chequered plates, wire rods, rods, hollow square/rectangular/round bars, tubes etc., anchor bolts, nuts, bolts, washers, screws, clamps, rivets, rubber pads, packing material with all necessary supports and accessories. The fabrication process shall be through electric arc welding method and cutting, drilling, riveting, bending shall be done by highly skilled workmanship. The surface shall be neatly finished with wire brushes before painting, all MS supports shall be painted using two coats of zincromate primer and two coats of metallic enamel paint. The fabrication shall be started after approval of load bearing calculations and shop drawings. The final fabricated and paint finished structure shall be approved by engineer-in-charge. mode of measurement shall be per kg of mild steel including painting cost. Note : 1) Color shall be as per client/architect. 2) Contractor shall take prior approval from client/consultant for using this line item. | [10 empty] | 10000 | Kgs | 100 | 56 | 1000000 | 560000 | 1560000
141 | MISCELLANEOUS | LABELLING & IDENTIFICATION | MECHANICAL IDENTIFICATION & LABELLING : Labelling, Tags, Markers, stickers paint, warning, operating lables, notice, schematics palcement at key locations as sepecified in the BS 1710/ ISO 14726 and as required at site and upto satisfaction of engineer. | [10 empty] | 1 | Lot | 0 | 68750 | 0 | 68750 | 68750
141 | MISCELLANEOUS | PAINTING | PAINTING : Painting on pipes with Alu-Zinc Primer & two coats of Epoxy. | [10 empty] | 200 | Sq.m | 360 | 125 | 72000 | 25000 | 97000
141 | MISCELLANEOUS | CRITICAL SPARES | SUPPLY OF CRITICAL SPARES AS PER MANUFACTURESR RECOMMENDATION FOR 5 Years of Operation for the Equipments listed in Section 5. | [10 empty] | QRO | Lot | 0 | 0 | 0 | 0 | 0
142 | MISCELLANEOUS | SENSOR FIXING | Installation of Smoke Sensor & Detectors supplied by Fire alarm system intergrator with necessary fittings and sealants as required to complete the installation. | [10 empty] | 250 | Nos. | 0 | 625 | 0 | 156250 | 156250
143 | MISCELLANEOUS | GRILLE FILTERS | Supply of Filters for return or Exhaust in criitcal areas EU4 to be mounted in the grilles or diffusers. | [10 empty] | QRO | Sqm | 2875 | 625 | 0 | 0 | 0
144 | MISCELLANEOUS | [12 empty] | QRO | Sqm | 0 | 0 | 0 | 0 | 0
|  |  | TOTAL VALUE OF HVAC WORKS EXCLUDING TAXES | [14 empty] | 197475910 | 32975154 | 230451064

## 3B Electrical Panel BOQ
SCHEDULE OF QUANTITIES FOR HVAC WORKS AT KIMS-SOUL SPACE, BANGALORE - CHILLER PLANT HVAC SYSTEM
All the rates quoted by the contractor shall be complete finished work including cost of all labour, material, scaffolding, finishing as required with tools, plants, lead, lift, taxes, tollage, octroi, royalties etc. except those specially excluded in the description of the individual items. All works shall be executed as per drawings, specification and instructions of Site incharge and shall include the supply and installation at site of all the equipment, ancillary materials as specified and all such items what-so-ever which may be required to fulfill the intent and purpose as laid down in the Design Basis report/ specification and/or the drawings. All materials shall be as per ISI specification and with IS certification marked wherever applicable. The material shall be duly approved by Site incharge before incorporation in the actual work.
S. No. | Item Description | Make/ Model for Reference | Unit | Qty. | MATERIAL |  | INSTALLATION
[5 empty] | RATE | AMOUNT | RATE | AMOUNT | REMARKS
SUB HEAD 'H' - ELECTRICAL WORKS
Preamble to BOQ for MCC , Distribution Boards & wall mounted Starter Panels
General Notes & Specifications as given below shall be applicable to all panels.The vendors shall consider the following details in their item rates, wherever required:
Supporting rigid steel framework.
Cubicle type, 14 gauge CRCA sheet steel enclosure.
Panel Complete with interconnections and distribution bus bars.
Proper bonding to earth.
Painting/lettering on Breakers and distribution boards, the location they serve, Providing on each panel its circuit diagram.
Providing cable clamps / supports within distribution boards cable alley.
TPN MCCBs shall mean 3 pole MCCBs with adequate size of neutral link.
All MCBs shall be of minimum 10 KA breaking capacity.
All motor feeders MCCBs shall be of motor duty and shall be able to carry the inrush current of motor.
Distribution panels shall be Powder Coated paint.
IP 65 for outdoor & IP 42 Indoor panels with proper enclosure.
All MCCB’s shall be provided with operating mechanism for door interlock.
Tinned copper earth bus shall be provided through out the length of each board.
All measuring instruments (Meters) shall be of digital electronic with LED of approved make and compatible with MODBUS.
All indicating lamps shall be LED type.
All current/voltage transformers shall be cast resin type.
All hinged door shall be earthed through 2.5 sq mm tinned braided copper wire.
All DOL & Star-Delta Starters shall be provided with voltage based SPPR (single phase preventor relay) and 2 nos. of Aux.Contacts for Remote operation/monitor.
The Panel fabricator shall provide Aluminium Bus-bars link from Breakers wherever more than two nos. of cables are terminated in the breakers.
Readymade 16SWG Sheet steel Enclosure with cutout For MCBs
The breaking capacity of MCCB’s shall be mentioned panel wise. All MCCB’s shall be with thermal magnetic releases upto 250 amps and miroprocessor based above 250 amps capacity, unless specified otherwise.
All internal control wiring shall be FRLS type.
Bus bar chamber shall be provided at top only. Incoming and outgoing cable entry shall be from top/bottom as required.
Live parts shall not be accessible after opening the door, Transparent acrylic sheet to be provided to cover the same.
Spare contacts of ACBs / MCCBs / Relay / Contactor shall be wired upto terminal block.
Design, fabrication, assembly, wiring and supply of front operated cubicle type compartmentalised as per Form 3B, rear access free standing, dust and vermin proof main switchboards suitable for use at 415 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of 35 kA at 415 volts, fabricated from 14 gauge CRCA sheet steel enclosure with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom and including lifting hooks and including GI earth strip of required size with 2 nos earthing terminals and including powder coated paint finish of approved shade over metal surface cleaned and treated with minimum seven tank process complete with interconnections etc as per specifications, as required and as below.
All outgoing shall be provided with Stop/Manual/ Auto selector switch to facilitate operation through BAS/BMS. All starters shall be provided with potential free Contacts for Connections to Building Automation/Management System.
A separate set of CTs to be provided for BAS and wiring from CT’s and voltage transducers to be brought on to separate set of terminals.
Note : MCCB’s shall be motor duty and suitable for 35 kA (ICS) fault current. ACB shall be suitable for 50 kA fault current.
The final breaker sizes may be changed based on final selection of Chiller. The cost shall be included in this panel and the contractor shall not charged extra cost in future.
No Panel to be manufactured without GA drawing approval.
A | MAIN HVAC PANEL ( Wherever VFD ask, Vendor to consider Space for it,VFD provided from client side)
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, sheet steel, wall mounted AHU starter panels including anchoring into the wall with following details:
All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contacts for Connections to Building Automation System.
The panel shall include the following components and accessories.
14G CRCA Powder Coated panel enclosure with earthing studs & hinged locable doors. IP54 Protection, suitable for 415V, 3 Phase, 4 wire, 50Hz system.
R,Y,B LED Type Phase indication lamps with control MCB's.
ON'/OFF/TRIP Indication LED Type lamp with control MCB.
Space for VFD (Variable Frequency Drive) which will have all inbuilt features like protection against over load, short circuit & single phasing. VFD shall have inbuilt auto / manual / BMS operation functions selection & shall be BMS compatible. Drive shall have ON/OFF/Trip displays & metering & display of electrical parameters.
View window to read VFD parameters.
For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
A fire detection relay module for tripping of AHU motor on receiving fire signal & fire damper interlocking. Necessary nos. of auxillary contactors & Relays shall be included in cost as required for the interlocking with smoke extraction fans & motorised firedampers.
Panel shall have adequate ventilation arrangement for heat dissipated by VFD.
The panel shall be as per IEC-61439 standard.
a. | POWER CONTROL PANEL-1 HVAC- (High Side)
1. | MAIN INCOMER |  |  | 1 | 1041518 | 1041518 | 187500 | 187500
i) | 1600A, ACB 3P, 50 KA MDO type with micro processor based protection for (O/C, S C, E/F) - 1 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | LED type Indicator for I/C power status , Red, yellow, green, 230VAC - 3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC - 3 Nos. | L&T |  |  | 0 |  | 0
iii) | VAF meter - 1 Nos. |  |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 15 VA Cast rasin CT - 1 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS |  |  |  | 0 |  | 0
i) | 630 Amp,MCCB TPN ,50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F) For 350 TR Water Cooled Chillers - 1 Nos. | L&T |  |  | 0 |  | 0
ii) | 630 Amp, MCCB TPN ,50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F) For 300 TR Water Cooled Chillers - 1 Nos. | L&T |  |  | 0 |  | 0
iii) | 400 Amp, MCCB TPN ,50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F) For VFD /Starter Panel-1 - 2 Nos. | L&T |  |  | 0 |  | 0
iv) | 63 Amp,MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 22 kw & 18.5 Kw Secondary Chilled Water Pump- 2 Nos. | L&T |  |  | 0 |  | 0
v) | 50 Amp, MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 15 kw Condenser Water Pump - 1 Nos. | L&T |  |  | 0 |  | 0
vi) | 32 Amp, MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 11 kw Primary Chilled Water Pump - 1 Nos. | L&T |  |  | 0 |  | 0
vii) | 25 Amp, MCCB TPN 10 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 7.5 kw Secondary Chilled Water Pump -1 Nos. | L&T |  |  | 0 |  | 0
viii) | 25 Amp, MCCB TPN 10 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 5.5 kw Cooling Tower Fan - 2 Nos. | L&T |  |  | 0 |  | 0
ix) | ON/off/Trip Indicator LED Type, Red,Green.Amber 230VAC (for each O/G feeder) - 27 Nos. | L&T |  |  | 0 |  | 0
x) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 15 VA Cast rasin CT with RS 485 (for each feeder except spare feeder ) |  |  |  | 0 |  | 0
xi) | Control Terminals Block 2.5 sq mm | Connectwell |  |  | 0 |  | 0
xii) | Power Terminals Block ( according to MCCB size) | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | BUSBAR and ENCLOSURE (Refer Annexure-1) |  |  |  | 0 |  | 0
| Busbar with 63% current density w.r.t. main I/C |  |  |  | 0 |  | 0
| All outgoing feeders shall be provided with operating handle, On indicating lamp with 2 A SP MCB protection & resin cast CT's class-1 suitable rating with digital Amps. Meter |  |  |  | 0 |  | 0
| Powder coated ,2MM/1.6MM. CRCA Sheet in 7 tank finish, and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | POWER CONTROL PANEL-2 HVAC- (High Side) |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 1612070 | 1612070 | 93750 | 93750
i) | 1600 Amp, ACB 3P, 50 KA MDO type with micro processor based protection for (O/C, S C, E/F) - 1 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.1 | BUS-COUPLER |  |  |  | 0 |  | 0
i) | 1600 Amp, ACB 3P, 50 KA MDO type with micro processor based protection for (O/C, S C, E/F) - 1 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | LED type Indicator for I/C power status , Red, yellow, green, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC - 3 Nos. | L&T |  |  | 0 |  | 0
iii) | VAF meter - 1 Nos. |  |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 15 VA Cast rasin CT - 1 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS |  |  |  | 0 |  | 0
i) | 1250 Amp, ACB 3P, 50 KA MDO type with micro processor based protection for (O/C, S C, E/F) For 350 TR Water Cooled Chillers (old) - 1 Nos. | L&T |  |  | 0 |  | 0
ii) | 630 Amp, MCCB TPN ,50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F) SPARE - 1 Nos. | L&T |  |  | 0 |  | 0
iii) | 400 Amp,MCCB TPN ,50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F) For VFD /Starter Panel-2 - 2 Nos. | L&T |  |  | 0 |  | 0
iv) | 63 Amp, MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 22 kw & 18.5 Kw Secondary Chilled Water Pump - 2 Nos. | L&T |  |  | 0 |  | 0
v) | 50 Amp, MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 15 kw Condenser Water Pump - 1 Nos. | L&T |  |  | 0 |  | 0
vi) | 32 Amp, MCCB TPN 50 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 11 kw Primary Chilled Water Pump - 1 Nos. | L&T |  |  | 0 |  | 0
vii) | 25 Amp, MCCB TPN 10 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 7.5 kw Secondary Chilled Water Pump - 1 Nos. | L&T |  |  | 0 |  | 0
viii) | 25 Amp, MCCB TPN 10 KA 4P, MDO type, thermal magnetic based release (O/C, S C, E/F), O/G FOR 5.5 kw Cooling Tower Fan - 2 Nos. | L&T |  |  | 0 |  | 0
ix) | ON/off/Trip Indicator LED Type, Red,Green.Amber 230VAC (for each O/G feeder) - 24 Nos. | L&T |  |  | 0 |  | 0
x) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 10 VA Cast rasin CT with RS 485 (for each feeder except spare feeder ) |  |  |  | 0 |  | 0
xi) | Control Terminals Block 2.5 sq mm | Connectwell |  |  | 0 |  | 0
xii) | Power Terminals Block ( according to MCCB size) | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | BUSBAR and ENCLOSURE (Refer Annexure-1) |  |  |  | 0 |  | 0
| Busbar with 63% current density w.r.t. main I/C |  |  |  | 0 |  | 0
| All outgoing feeders shall be provided with operating handle, On indicating lamp with 2 A SP MCB protection & resin cast CT's class-1 suitable rating with digital Amps. Meter |  |  |  | 0 |  | 0
| Powder coated ,2MM/1.6MM. CRCA Sheet in 7 tank finish, and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
c. | VFD/Starter Panel-1 (High Side) |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  |  | 0 |  | 0
i) | MCCB 400A 3P, 50 KA with micro processor based protection for (O/C, S C, E/F)-- 1 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  | 1 | 985486 | 985486 | 93750 | 93750
i) | MCB TP 6A for indication lamp - 1 Nos. | L&T |  |  | 0 |  | 0
ii) | MCB SP 6A for control - 1 Nos. | L&T |  |  | 0 |  | 0
iii) | LED type Indicator for I/C power status , Red, yellow, green, 230VAC - 3 Nos. | L&T | Nos. |  | 0 |  | 0
iv) | LED type Indicator for MCCB on/off/Trip Red, Green/Amber, 230VAC - 3 Nos. | L&T |  |  | 0 |  | 0
v) | VAF meter - 1 Nos. |  |  |  | 0 |  | 0
vi) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 15 VA Cast rasin CT - 1 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G Feeders |  |  |  | 0 |  | 0
3.1 | Primary Chilled Water Pump (11.0 KW) VFD / Bypass Y-Δ Starter - 02 Nos. |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP 32, Iq 50kA - 01 Nos. | L&T MOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 50 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| 50 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| OLR (9-15A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 03 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Secondary Chilled Water Pump-shaft -1 (22.0 KW) VFD / Bypass Y-Δ Starter - 01 Nos. + 1 spare |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP 63 A, Iq 50kA - 01 Nos. | L&T MOG-H2M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| OLR (20-33A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Secondary Chilled Water Pump-shaft -2 (7.5 KW) VFD / Bypass Y-Δ Starter - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(11-16 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Secondary Chilled Water Pump-shaft -3 (18.5 KW) VFD / Bypass Y-Δ Starter - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(28-40 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. | elmex |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. | elmex |  |  | 0 |  | 0
| Power Wire - 4 sq mm | polycab/RR Kabel FRLS |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Condenser Water Pump (15 KW) VFD / Bypass Y-Δ Starter - 02 Nos. |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(24-32 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 50 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| 50 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| PLA plug in type rlaty |  |  |  | 0 |  | 0
| Power Terminal (Bus bar Type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Cooling Tower Fan (5.5 KW) VFD / Bypass DOL Starter - 04 Nos. + 1 spare |  | Nos. | 5 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(9 - 13 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25 A Power contactor - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25 A Power contactor (VFD I/P, O/P) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (Bus bar Type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
d. | VFD/Starter Panel-2 (High Side) |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  |  | 0 |  | 0
i) | MCCB 400A 3P, 50 KA with micro processor based protection for (O/C, S C, E/F) - 1 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  | 1 | 944636 | 944636 | 93750 | 93750
i) | MCB TP 6A for indication lamp - 1 Nos. | L&T |  |  | 0 |  | 0
ii) | MCB SP 6A for control - 1 Nos. | L&T |  |  | 0 |  | 0
iii) | LED type Indicator for I/C power status , Red, yellow, green, 230VAC - 3 Nos. | L&T | Nos. |  | 0 |  | 0
iv) | LED type Indicator for MCCB on/off/Trip Red, Green/Amber, 230VAC - 3 Nos. | L&T |  |  | 0 |  | 0
v) | VAF meter - 1 Nos. |  |  |  | 0 |  | 0
vi) | Energy meter Entes/Selec/Trinity (True RMS) with communication port & Cl 0.5, 15 VA Cast rasin CT - 1 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G Feeders |  |  |  | 0 |  | 0
3.1 | Primary Chilled Water Pump (11.0 KW) VFD / Bypass Y-Δ Starter - 02 Nos. |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(19-25 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 40 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 40 |  |  | 0 |  | 0
| 40 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 40 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Secondary Chilled Water Pump-shaft -1 (22.0 KW) VFD / Bypass Y-Δ Starter - 01 Nos. + 1 spare |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(35-50 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (bus bar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Secondary Chilled Water Pump-shaft -2 (7.5 KW) VFD / Bypass Y-Δ Starter - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(11-16 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Secondary Chilled Water Pump-shaft -3 (18.5 KW) VFD / Bypass Y-Δ Starter - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(28-40 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. | elmex |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. | elmex |  |  | 0 |  | 0
| Power Wire - 4 sq mm | polycab/RR Kabel FRLS |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Condenser Water Pump (15 KW) VFD / Bypass Y-Δ Starter - 02 Nos. |  | Nos. | 2 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(24-32 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 50 A Power contactor (star-Delta Starter) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| 50 A Power contactor (VFD I/P, O/P & Isolation) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | We have not quoted for this item,as it is captured in main panel
3.6 | Cooling Tower Fan (5.5 KW) VFD / Bypass DOL Starter - 04 Nos. + 1 spare |  | Nos. | 5 | 0 | 0 | 0 | 0
| MPCB TP(9 - 13 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25 A Power contactor - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25 A Power contactor (VFD I/P, O/P) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-delay timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Power Terminal (busbar type) 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | Smoke spill Axial flow fan- DOL Starter (3KW) - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | CHW PAC Unit- DOL Starter (1.9KW) - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
3.9 | CHW Air handling unit- DOL Starter (1.8KW) - 01 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | EA Cabinet Fan- DOL Starter (1.5KW) - 1 Nos. |  | Nos. | 1 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.11 | EA Cabinet Fan- DOL Starter (1.1KW) - 02 Nos. + 1 Spare |  | Nos. | 3 | 0 | 0 | 0 | 0 | We have not quoted for this item,as it is captured in main panel
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B. | POWER DISTRIBUTION BOARD |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B1. | LOWER BASEMENT |  |  |  | 0 |  | 0
a. | FOR LOWER BASEMENT-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 1219347 | 2438694 | 187500 | 375000
i) | 400A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve- 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port- 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 400/5 CT, 10VA Burden, Class-1- 03 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | EA Centrifugal fan -(15KW) - 04 Nos. +1 Spare |  |  |  | 0 |  | 0
i) | 50A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | FA Axial flow fan-(7KW) - 02 Nos. + 1 Spare |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | EA Cabinet Fan - (5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Smoke spill Axial flow fan(fire -(5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Celing Suspended AHUs -(1.6KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Jet Fan - (1.5KW) - 13 Nos. + 03 Nos. Spare |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Celing Suspended AHUs - (1.2KW) - 02 Nos. + 1 Spare |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Celing Suspended AHUs - (1KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Celing Suspended AHUs - (0.8KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1ø Load - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 | Nos. |  | 0 |  | 0
ii) | ON /Trip Indicator, Red,Amber 230VAC - 02 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 3C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | EA Cabinet Fan (1.5 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 16A MCB DP, C -Curve Iq 10kA - 1Nos. | BB20160C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | Smoke spill Axial flow fan (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 1Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 1Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | 4way Cassette unit (0.2 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.8 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 1Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Inline Fan (0.2 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | 4way Cassette unit (0.07 Kw) - 08Nos. + 2 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | 4way Cassette unit (0.13 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.9 | 1way Cassette unit (0.04 Kw) - 02Nos. + 1 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | VAV (150 dia) (0.05 Kw) - 20Nos. |  |  |  | 0 |  | 0
i) | 06A, MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR LOWER BASEMENT-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 697381 | 697381 | 93750 | 93750
i) | 150A TPN Microprocessor release 50KA MCCB - 1 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve- 1 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port- 1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 150/5 CT, 10VA Burden, Class-1 - 3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | FA Axial flow fan-(7KW) - 02 Nos. + 1 Spare |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Jet Fan - (1.5KW) - 13 Nos. + 03 Nos. Spare |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | O/G Feeder for 1 ø |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) |  |  |  | 0 |  | 0
4.1 | Exhaust Fan (0.6 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | Fresh Air Fan (0.6 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | FCU (0.4 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | Exhaust Fan (0.2 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | CSU (0.1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B2. | UPPER BASEMENT |  |  |  | 0 |  | 0
a. | FOR UPPER BASEMENT-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 1216337 | 1216337 | 187500 | 187500
i) | 630A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 600/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | EA Centrifugal fan -(15KW) - 04 Nos. +1 Spare |  |  |  | 0 |  | 0
i) | 50A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | FA Axial flow fan - (8KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | EA Cabinet Fan- (6KW) - 04 Nos. +1 spare |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | FA Cabinet Fan -(6KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Smoke spill Axial flow fan(fire) -(4KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan - (4KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | EA Cabinet Fan - (4KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | EA Cabinet Fan - (2KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | Jet Fan - (1.5KW) - 12 Nos. + Spare 2 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | EA Cabinet Fan - (1.1KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.11 | Celing Suspended AHUs - (1 KW) - 2 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.12 | O/G Feeder for 1 ø |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR UPPER BASEMENT-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 791738 | 791738 | 93750 | 93750
i) | 150A TPN Microprocessor release 50KA MCCB | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 600/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | FA Axial flow fan - (7KW) - 02 Nos. + 01 Nos. Spare |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | EA Centrifugal fan - (3KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | FA Centrifugal fan - (2KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | FA Centrifugal fan - (1.5 KW) - 12 Nos. + Spare 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | O/G Feeder for 1 ø |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B3. | GROUND FLOOR |  |  |  | 0 |  | 0
a. | FOR GROUND FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 448102 | 448102 | 93750 | 93750
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 600/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Ceiling Suspended Unit - (3.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Ceiling Suspended Unit - (3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Air Handling Unit - (3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Celing Suspended AHUs -(2.1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | EA Cabinet Fan - (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Celing Suspended Unit - - (1.1KW) - 2 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | EA Cabinet Fan - - (1.1KW) - 2 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1ø Load - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON /Trip Indicator, Red,Amber 230VAC - 02 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | CHW High static Fan coil unit( 0.15 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | 1 way Cassette unit (0.04 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | 4way Cassette unit (0.2 Kw) - 04 Nos. + 1 nos. spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | CHW Fan Coil Unit (0.2 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | CHW Hi-wall unit (0.15 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | EA Cabinet Fan (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | EA Inline Fan (0.2 Kw) - 05Nos. + 2nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.9 | EA Propeller Fan (0.03 Kw) - 02Nos. + 1 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | VAV (150 dia) (0.05 Kw) - 20Nos. + 4 Nos Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR GROUND FLOOR-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 358195 | 716390 | 93750 | 187500
i) | 100A TPN Microprocessor release 50KA MCCB- 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 600/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | EA Centrifugal fan -(15KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 50A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | EA Cabinet Fan -(1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Celing Suspended AHUs -(1.4KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Celing Suspended AHUs - (0.55KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 3C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | CHW Hi-wall unit (0.05 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fan (0.05 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (0.2 Kw) - 03Nos. + 1nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Propeller Fan (0.03 Kw) - 03Nos. + 1 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | VAV (150 dia) (0.05 Kw) - 06Nos. + 1 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | VAV (400 dia) (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | CHW High static Fan coil unit( 0.15 Kw) - 23Nos. + 4 Nos. spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B4. | FIRST FLOOR |  |  |  | 0 |  | 0
a. | FOR FIRST FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 348152 | 696304 | 62500 | 125000
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 50/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit - (11 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 40A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | CHW Ceiling Suspended Unit - (2.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | CHW Ceiling Suspended Unit- (2KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 10A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | EA Cabinet Fan- (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Ceiling Suspended Unit (1.3KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | CHW Ceiling Suspended Unit (1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | CHW Ceiling Suspended Unit (0.8KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | CHW High static Fan Coil Unit (0.20 Kw) - 03Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | 4way Cassette Unit (0.2 Kw) - 06Nos. + 2 Nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | CHW Hi-wall unit (0.07 Kw) - 03 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Cabinet Fan (0.2 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Inline Fan (0.2 Kw) - 04Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | EA Propeller Fan (0.35 Kw) - 04 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | VA Valve (0.05 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | VAV (150. dia) (0.05 Kw) - 32 Nos. + 4 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR FIRST FLOOR-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 358195 | 716390 | 62500 | 125000
i) | 63A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 50/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit - (18.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | EA Cabinet Fan- (1.5 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | EA Cabinet Fan- (0.55 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | O/G Feeder for 1 ø - PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | O/G Feeder for 1 ø - PDB-2 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) -PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | O/G FEEDERS (1 ø ) -PDB-1 |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | CHW Hi-wall unit (0.05 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fan (0.37 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (0.35 Kw) - 03 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Propeller Fan (0.03 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | VAV (350 dia) (0.05 Kw) - 15Nos. + 1 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | VAV (150 dia) (0.05 Kw) - 29Nos. + 5 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B5. | SECOND FLOOR |  |  |  | 0 |  | 0
a. | FOR SECOND FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 358195 | 358195 | 62500 | 62500
i) | 150A TPN Microprocessor release 50KA MCCB | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
iii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with RS 485 communication port &150/5 cast resin CT, 10VA Burden, Class-0.5 -3 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit- (4KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 12A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DNO 100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | EA Cabinet Fan (3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 8A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Ceiling Suspended Unit (1.8KW) - 02 Nos.+ 1 spare |  |  |  | 0 |  | 0
i) | 6A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Celing Suspended AHUs (EC Fan)- (1.5KW) - 02 Nos.+ 1 spare |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Ceiling Suspended Unit - (1.2KW) - 02 Nos. + 1 Spare |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan - (1.1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 3A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | Celing Suspended AHUs - (1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 3A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | Celing Suspended AHUs - (0.8KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 3A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | Celing Suspended AHUs - (0.6KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 3A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | O/G Feeder for 1 ø- PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. |  |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø )PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) PDB-1 |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | EA Cabinet Fan (0.6 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fan (0.37 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (0.35 Kw) - 03 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | Hugh Statis Fan coil unit (0.22 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | CHW Fan coil unit (0.2 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | CHW Hi-wall unit (0.15 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.9 | Drain Pump (VRF) (0.25 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.1 | EA Propeller Fan (0.03 Kw) - 06 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR SECOND FLOOR- Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 265767 | 265767 | 62500 | 62500
i) | 150A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 150/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit - (18.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 63A MCCB TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | CHW Air handling unit - (3 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 8A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | CHW Air handling unit -(1.5 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | CHW Air handling unit -(1.3 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Air handling unit - (0.55 KW) - 1 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | O/G Feeder for 1 ø - PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | EA Cabinet Fan (0.37 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Inline Fan (0.35 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (0.20 Kw) - 05 Nos. + 01 Nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | CHW Hi-wall unit (0.14 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Propeller Fan (0.03 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | VA Valve (0.05 Kw) - 03 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B6. | THIRD FLOOR |  |  |  | 0 |  | 0
a. | FOR THIRD FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 466160 | 932320 | 62500 | 125000
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
iii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with RS 485 communication port &100/5 cast resin CT, 10VA Burden, Class-0.5 -3 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Air Handling Unit (EC Fan)- DOL Starter (2.2 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 7.5A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Ceiling Suspended Unit (EC Fan)- DOL Starter (2.1 KW) - 02 Nos.+1 Spare |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Air Handling Unit (EC Fan)- DOL Starter (1.6 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 4A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | EA Cabinet Fan (EC Fan)- DOL Starter (1.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 2.5A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Air Handling Unit (EC Fan)- DOL Starter (1.2 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 2.5A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Ceiling Suspended Unit (EC Fan)- DOL Starter (1.2 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 2A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | EA Cabinet Fan- DOL Starter (1.1KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 2A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | Air Handling Unit (Plug Fan)- DOL Starter (1 KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 2A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | Ceiling Suspended Unit (Plug Fan)- DOL Starter (0.8 KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 2A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.11 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Smoke spill Axial flow fan (1.5 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 16A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20160C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fanl (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (Booster Fan ) (0.35 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.18 Kw) - 07Nos. + 2 Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | 4way Cassette unit (0.13 Kw) - 09Nos. +2 Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.2 | EA Propeller Fan (0.03 Kw) - 03Nos. + 1 Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR THIRD FLOOR-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 269158 | 538316 | 62500 | 125000
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
iii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with RS 485 communication port &100/5 cast resin CT, 10VA Burden, Class-0.5 -3 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit- VFD/Y-∆ Starter(10KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 40A MCCB(L&T DN0-100M) TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | CHW Air handling unit - DOL Starter (5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB(L&T DN0-100M) TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Smoke spill Axial flow fan- DOL Starter (5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 32A MCCB(L&T DN0-100M) TPN, Iq 50kA - 01 Nos. | L&T DN0-100M |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | EA Cabinet Fan (EC Fan)- DOL Starter (2.2 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | EA Cabinet Fan (EC Fan)- DOL Starter (1.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 2.5A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan (EC Fan)- DOL Starter (0.55 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 2A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | CHW Fan coil unit (0.15 Kw) - 17Nos. + 3 nos spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | 4way Cassette unit (0.19 Kw) - 06Nos. + 3 nos spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.2 | CHW Hi-wall unit (0.05 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.3 | EA Cabinet Fan (0.37 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.4 | EA Inline Fan (Booster Fan) (0.35 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.5 | High static Fan coil unit (0.15 Kw) - 04Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5.6 | VAV (150 dia) - 08Nos. + 02 Sapre |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B7. | FOURTH FLOOR |  |  |  | 0 |  | 0
a. | FOR FOURTH FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 390284 | 780568 | 62500 | 125000
i) | 100A TPN Microprocessor release 50KA MCCB- 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 100/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Smoke Spill Axial flow fan - (3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Smoke spill Axial flow fan - (2.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | CHW Air handling unit - (2.4 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | Ceiling Suspended Unit- (2.3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Air handling unit -(1.8 KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan- (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | Celing Suspended AHUs - (1.3KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | EA Cabinet Fan- (1.1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | Celing Suspended AHUs - (1KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | Celing Suspended AHUs -(0.8KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.11 | Celing Suspended AHUs -(0.6KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.12 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.13 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 2.5sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Smoke spill Axial flow fan (1.5 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 16A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20160C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | 4way Cassette unit (0.15 Kw) - 08Nos. + 2 Nos. Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | CHW Hi-wall unit (0.05 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Cabinet Fan (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Inline Fan (0.2 Kw) - 09Nos. + 2 Nos. Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | EA Propeller Fan (0.03 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | CHW Fan Coil Unit (0.15 Kw) - 17Nos. + 3 Nos. Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR FOURTH FLOOR-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 255181 | 510362 | 62500 | 125000
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 100/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Smoke Spill Axial flow fan - (5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Smoke spill Axial flow fan - (2.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | EA Cabinet Fan - (2.2 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | EA Cabinet Fan- (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | Celing Suspended AHUs - (1.3KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan -(0.55KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 4C x 2.5sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | High Static Fan Coil Unit (0.2Kw) - 06 Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | 4way Cassette unit (0.15 Kw) - 09 Nos. + 2 Nos. Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | CHW Hi-wall unit (0.05 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Cabinet Fan (0.35 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Inline Booster Fan (0.2 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | CHW Fan Coil Unit (0.2 Kw) - 23 Nos. + 4 Nos. Spare |  |  |  | 0 |  | 0
i) | 6A MCB DP, C -Curve Iq 10kA -1 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm -3 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B8. | FIFTH FLOOR |  |  |  | 0 |  | 0
a. | FOR FIFTH FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 266666 | 533332 | 62500 | 125000
i) | 63A TPN Microprocessor release 50KA MCCB- 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 50/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Smoke spill Axial flow fan - (4 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Smoke spill Axial flow fan - (3 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | CHW PAC Unit- (1.9KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | CHW PAC Unit- (1.8KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | EA Cabinet Fan (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan (1.1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1 ø (PDB-1) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1 ø (PDB-2) |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-1) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-1 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) (PDB-1) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | EA Cabinet Fan (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | CHW High static Fan coil unit (0.2 Kw) - 06Nos. + 2 Nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | 4way Cassette unit (0.07 Kw) - 04 Nos. + 1 Nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Inline Fan (0.35 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | EA Propeller Fan (0.35 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | CHW Fan coil unit (0.15 Kw) - 19Nos. + 4 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR FIFTH FLOOR-Right Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 2 | 278152 | 556304 | 43750 | 87500
i) | 63A TPN Microprocessor release 50KA MCCB | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 50/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | Smoke spill Axial flow fan - (5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | Smoke spill Axial flow fan - (4 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | EA Cabinet Fan (1.5KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | CHW Ceiling Suspended Unit (1.3KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Ceiling Suspended Unit (0.8KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | EA Cabinet Fan (0.55KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | O/G Feeder for 1 ø - PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | O/G Feeder for 1 ø - PDB-2 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) -PDB-1 |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) -PDB-1 |  |  |  | 0 |  | 0
4.1 | CHW High static Fan Coil Unit (0.15 kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | 4way Cassette unit (0.07 Kw) - 05 Nos. + 1 Nos spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | CHW Hi-wall unit (0.05 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Cabinet Fan (0.2 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.1 Kw) - 04 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | Fire damper control Panel (1 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | Main I/C FEEDERS (1 ø ) - 01 Nos (PDB-2) |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: PDB-2 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
5 | O/G FEEDERS (1 ø ) (PDB-2) |  |  |  | 0 |  | 0
5.1 | CHW Fan coil unit (0.15 Kw) - 22Nos. + 4 Nos. Spare |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
B9. | SIXTH FLOOR |  |  |  | 0 |  | 0
a. | FOR SIXTH FLOOR-Left Zone |  |  |  | 0 |  | 0
1. | MAIN INCOMER |  |  | 1 | 466160 | 466160 | 62500 | 62500
i) | 200A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | LED type Indicator for ACB on/off/Trip Red, Green/Amber, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
iii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T |  |  | 0 |  | 0
iv) | Energy meter Entes/Selec/Trinity (True RMS) with RS 485 communication port & 200/5 cast resin CT, 10VA Burden, Class-0.5 -3 Nos. | Entes/Selec/Trinity |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Air handling unit-(7.3 KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB(L&T DM16) TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 6 sq.mm - 04 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | CHW Air handling unit-(5.0 KW) - 08 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | Smoke spill Axial flow fan-(5.0 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | CHW Ttreated fresh air unit-(4 KW) -01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | CHW Ceiling suspended unit-(1.9KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | Celing Suspended AHUs EC Fan)-(1.3KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | EA Cabinet Fan- (1.1KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | CHW Ceiling suspended unit-(0.8KW) - 04 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | O/G Feeder for 1 ø |  |  |  | 0 |  | 0
i) | 25A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) - 01 Nos |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA -1 No. | L&T DM 16 |  |  | 0 |  | 0
ii) | Incoming Cable: 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | O/G FEEDERS (1 ø ) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | EA Cabinet Fan (0.95 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fan (0.75 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | CHW Fan coil unit (0.36 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.35 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | EA Cabinet Fan (0.55 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | CHW High static Fan coil unit (0.18 Kw) - 02 Nos |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | CHW Hi-wall unit (0.14 kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.9 | CHW 4way Cassette unit (0.13 kw) - 04 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.1 | EA Inline Fan (0.09 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.11 | VAV (150 dia) (0.05 Kw) - 03 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.12 | EA Propeller Fan(0.2 Kw) - 02 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
6 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | FOR SIXTH FLOOR-Right Zone |  |  |  | 0 |  | 0
1 | MAIN INCOMER |  |  | 1 | 454674 | 454674 | 62500 | 62500
i) | 100A TPN Microprocessor release 50KA MCCB - 01 Nos. | L&T DM 100 |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
2 | METERING WITH CONTROLING SYSTEMS |  |  |  | 0 |  | 0
i) | Power Indicator LED type Red, yellow, Blue, 230VAC -3 Nos. | L&T |  |  | 0 |  | 0
ii) | Control MCB 1P 6A 10kA C Curve - 01 Nos. |  |  |  | 0 |  | 0
iii) | Energy meter (MFM) with RS 485 communication port - 01 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
iv) | 100/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3 | O/G FEEDERS (3 ø ) |  |  |  | 0 |  | 0
3.1 | CHW Ceiling suspended unit-(3.1 KW) - 01 Nos |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.2 | CHW Air handling unit-(3 KW) - 01 Nos |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.3 | CHW Air handling unit- (2.9 KW) - 01 Nos |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.4 | CHW Air handling unit-(2.4KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.5 | EA Cabinet Fan-(2.2KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 8 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.6 | CHW Air handling unit- (1.7 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.7 | CHW Air handling unit- (1.6 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.8 | EA Cabinet Fan- (1.5 KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 16A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.9 | CHW Ceiling suspended unit-(1.1KW) - 05 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.1 | CHW Ceiling suspended unit- (1.0KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.11 | CHW Ceiling suspended unit- (0.8KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.12 | CHW Ceiling suspended unit- (0.7KW) - 02 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.13 | EA Cabinet Fan- (0.55KW) - 01 Nos. |  |  |  | 0 |  | 0
i) | 6A MCCB TPN, Iq 50kA - 01 Nos. | L&T DM 16 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC - 01 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal (Bus-bar Type) 4 sq.mm - 04 Nos. | Elmex/Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
3.14 | O/G Feeder for 1 ø |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA -1 Nos. | L&T DM 100 |  |  | 0 |  | 0
ii) | ON Indicator, Red, 230VAC -1 Nos. | L&T |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm -4 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
vi) | Control MCB 1P 6A 10kA C Curve -1 Nos. |  |  |  | 0 |  | 0
v) | Energy meter (MFM) with RS 485 communication port -1 Nos. | SELEC/Entes/Trinity |  |  | 0 |  | 0
vi) | 25/5 CT, 10VA Burden, Class-1 -3 Nos. |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4 | Main I/C FEEDERS (1 ø ) |  |  |  | 0 |  | 0
i) | 32A MCCB TPN, Iq 50kA -1 No. | L&T DM 100 |  |  | 0 |  | 0
ii) | Incoming Cable: 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  |  |  | 0 |  | 0
4 | O/G FEEDERS (1 ø ) |  |  |  | 0 |  | 0
4.1 | Fire damper control Panel (1 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 10A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20100C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.2 | Smoke spill Axial flow fan (1.5 Kw) - 02Nos. |  |  |  | 0 |  | 0
i) | 16A MCB DP, C -Curve Iq 10kA - 01 Nos. | BB20160C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.3 | EA Cabinet Fan (0.37 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.4 | EA Inline Fan (0.35 Kw) - 01Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.5 | EA Inline Fan (0.18 Kw) - 01 Nos |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.6 | CHW Hi-wall unit (0.14 kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.7 | EA Inline Fan (0.09 Kw) - 06 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.8 | 4way Cassette unit (0.07 Kw) - 01 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.9 | VAV (150 dia) (0.05 Kw) - 07 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
iii) | Power Terminal 4 sq.mm - 03 Nos. | Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
4.1 | EA Propeller Fan(0.2 Kw) - 04 Nos. |  |  |  | 0 |  | 0
i) | 06A MCB DP, C Curve Iq 10kA - 01 Nos. | BB20060C |  |  | 0 |  | 0
ii) | Power Terminal 4 sq.mm - 03 Nos. | Elmex/Connectwell |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
5 | BUSBAR and ENCLOSURE |  |  |  | 0 |  | 0
i) | Powder coated ,2MM/1.6MM. CRCA Sheet in tether finish, 1and front Siemens gray color or as per your choice . Size of PANEL( H-MM X L-MM X D-MM ) | JINDAL |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C. | Starter Panel- Floor Wise |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C1. | LOWER BASEMENT |  |  |  | 0 |  | 0
a. | Floor-Lower Basement (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | EA Centrifugal fan - VFD/Y-∆ Starter (15KW) - 04 Nos. +1 Spare |  | Nos. | 5 | 124174 | 620870 | 62500 | 312500
| MPCB TP 50 A, Iq 50kA - 01 Nos. | L&T MOG-H2M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 40A Power contactor (star) - 01 Nos. | L&T MNX 40 |  |  | 0 |  | 0
| 70A Power contactor (Main & Delta) - 02 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70A Power contactor for VFD (I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| OLR (14-23A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | FA Axial flow fan (EC Fan)- DOL Starter (7KW) - 02 Nos. + 1 Spare |  | Nos. | 3 | 61793 | 185379 | 18750 | 56250
| MPCB TP(11-16 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (Main, Start & DeltaL) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | EA Cabinet Fan - DOL Starter (5 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | Smoke spill Axial flow fan(fire)- DOL Starter (5KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | Celing Suspended AHUs - DOL Starter (1.6KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | Jet Fan (Plug Fan)- DOL Starter (1.5KW) - 13 Nos. + 03 Nos. Spare |  | Nos. | 16 | 59439 | 951024 | 62500 | 1000000
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | EA Cabinet Fan (Plug Fan)- DOL Starter (1.5KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 62500 | 62500
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | Celing Suspended AHUs - DOL Starter (1.2KW) - 02 Nos. + 1 Spare |  | Nos. | 3 | 88864 | 266592 | 18750 | 56250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | Celing Suspended AHUs - DOL Starter (1KW) - 02 Nos. |  | Nos. | 2 | 50023 | 100046 | 18750 | 37500
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.1 | Celing Suspended AHUs - DOL Starter (0.8KW) - 02 Nos. |  | Nos. | 2 | 50023 | 100046 | 18750 | 37500
| MPCB TP(1.6 - 2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-Lower Basement (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | FA Axial flow fan - Y-∆ Starter (7 KW) - 02 Nos. + 01 Nos. Spare |  | Nos. | 3 | 33545 | 100635 | 18750 | 56250
| MPCB TP 25, Iq 50kA - 01 Nos. | L&TMOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (Start, Delta & Main) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P & Isolation ) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| OLR (6-10), Iq 50kA - 01 Nos. | L&T MN2 |  |  | 0 |  | 0
| ON-Delay Timer - 01 Nos. | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | FA Centrifugal fan - DOL Starter (1.5 KW) - 13 Nos. + 2 Spares |  | Nos. | 15 | 30014 | 450210 | 62500 | 937500
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| 12A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C2. | UPPER BASEMENT |  |  |  | 0 |  | 0
a. | Floor-UBF Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | EA Centrifugal fan - Y-∆ Starter Starter (15KW) - 04 Nos. +1 Spare |  | Nos. | 5 | 124174 | 620870 | 62500 | 312500
| MPCB TP 50 A, Iq 50kA - 01 Nos. | L&T MOG-H2M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 40A Power contactor (star) - 01 Nos. | L&T MNX 40 |  |  | 0 |  | 0
| 70A Power contactor (Main & Delta) - 02 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70A Power contactor for VFD (I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| OLR (14-23A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 8 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire (FRLS)- 6 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | FA Axial flow fan (EC Fan)- Y-∆ Starter Starter (8 KW) - 01 Nos. |  | Nos. | 1 | 34722 | 34722 | 9375 | 9375
| MPCB TP(11-16 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (Main, Start & DeltaL) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 6 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | EA Cabinet Fan - DOL Starter (6 KW) - 04 Nos. + 01 Nos. Spare |  | Nos. | 5 | 59439 | 297195 | 18750 | 93750
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | FA Cabinet Fan - DOL Starter (6 KW) - 02 Nos. |  | Nos. | 2 | 30014 | 60028 | 9375 | 18750
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | Smoke spill Axial flow fan(fire)- DOL Starter (4KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan (Plug Fan)- DOL Starter (2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 9375 | 9375
| MPCB TP(4 - 6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | Jet Fan (Plug Fan)- DOL Starter (1.5KW) - 12 Nos. + 02 Nos. Spare |  | Nos. | 2 | 50023 | 100046 | 62500 | 125000
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | EA Cabinet Fan- DOL Starter (1.1 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | Celing Suspended AHUs - DOL Starter (1KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-UBF Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | FA Axial flow fan - Y-∆ Starter (7 KW) - 02 Nos. + 01 Nos. Spare |  | Nos. | 3 | 59439 | 178317 | 18750 | 56250
| MPCB TP 25, Iq 50kA - 01 Nos. | L&TMOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (Start, Delta & Main) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P & Isolation ) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| OLR (6-10), Iq 50kA - 01 Nos. | L&T MN2 |  |  | 0 |  | 0
| ON-Delay Timer - 01 Nos. | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | EA Centrifugal fan - DOL Starter (3 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | FA Centrifugal fan - DOL Starter (2 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(4 - 6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| 22A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | FA Centrifugal fan - DOL Starter (1.5 KW) - 12 Nos. |  | Nos. | 12 | 30014 | 360168 | 93750 | 1125000
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| 12A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C3. | GROUND FLOOR |  |  |  | 0 |  | 0
a. | Floor-GF Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Ceiling Suspended Unit- DOL Starter (3.5KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Ceiling Suspended Unit- DOL Starter (3 KW) - 02 Nos. |  | Nos. | 2 | 30014 | 60028 | 18750 | 37500
| MPCB TP(4-6.3A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| 22A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | Air Handling Unit- DOL Starter (3 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(4-6.3A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| 22A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | Ceiling Suspended Unit- DOL Starter (2.1 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | EA Cabinet Fan - DOL Starter (1.5 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | Celing Suspended Unit - DOL Starter (1.1 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | EA Cabinet Fan - DOL Starter (1.1 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-GF Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air Handling Unit - VFD/Y-∆ Starter (15KW) - 01 Nos. |  | Nos. | 1 | 50023 | 50023 | 9375 | 9375
| MPCB TP 50 A, Iq 50kA - 01 Nos. | L&T MOG-H2M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 40A Power contactor (star) - 01 Nos. | L&T MNX 40 |  |  | 0 |  | 0
| 70A Power contactor (Main & Delta) - 02 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70A Power contactor for VFD (I/P, O/P & Isolation) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| OLR (14-23A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | EA Cabnetl fan - DOL Starter (1.5 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | Ceiling Suspended Unit - DOL Starter (1.4 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabnetl fan - DOL Starter (0.55 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 2.5 sq.mm - 8 Nos. | Elmex / Connectwell |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. | Elmex / Connectwell |  |  | 0 |  | 0
| Power Wire - 1.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C4. | FIRST FLOOR |  |  |  | 0 |  | 0
a. | Floor-1F Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air handling unit - Y-∆ Starter (11 KW) - 01 Nos. |  | Nos. | 1 | 38253 | 38253 | 9375 | 9375
| MPCB TP 32, Iq 50kA - 01 Nos. | L&TMOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 50A Power contactor (Start, Delta & Main) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| 50A Power contactor for VFD (I/P, O/P & Isolation ) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| OLR (9-15), Iq 50kA - 01 Nos. | L&T MN2 |  |  | 0 |  | 0
| ON-Delay (Y-∆) Timer - 01 Nos. | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | CHW Ceiling Suspended Unit- DOL Starter (2.5KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW Ceiling Suspended Unit - DOL Starter (2KW) - 02 Nos. |  | Nos. | 1 | 24129 | 24129 | 9375 | 9375
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabinet Fan- DOL Starter (1.5KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Ceiling Suspended Unit- DOL Starter (1.3KW) - 2 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | CHW Ceiling Suspended Unit- DOL Starter (1KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | CHW Ceiling Suspended Unit - DOL Starter (0.8KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-1F Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air handling unit - Y-∆ Starter (18.5 KW) - 01 Nos. |  | Nos. | 1 | 57085 | 57085 | 9375 | 9375
| MPCB TP 50, Iq 50kA - 01 Nos. | L&TMOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70A Power contactor (Start, Delta & Main) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| 70A Power contactor for VFD (I/P, O/P & Isolation ) - 03 Nos. | L&T MNX 70 |  |  | 0 |  | 0
| OLR (20-33), Iq 50kA - 01 Nos. | L&T MN2 |  |  | 0 |  | 0
| ON-Delay (Y-∆) Timer - 01 Nos. | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | EA Cabinet Fan- DOL Starter (1.5 KW) - 1 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| 12A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | EA Cabinet Fan- DOL Starter (0.55 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C5. | SECOND FLOOR |  |  |  | 0 |  | 0
a. | Floor-2F Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  | Nos. | 1 | 30014 | 30014 | 6250 | 6250
1.1 | CHW Air handling unit- DOL Starter (4KW) - 01 Nos. |  |  |  | 0 |  | 0
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| 22A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | EA Cabinet Fan - DOL Starter (3KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 6250 | 6250
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW Ceiling Suspended Unit- DOL Starter (1.8KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabinet Fan- DOL Starter (1.5KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Ceiling Suspended Unit - DOL Starter (1.2KW) - 02 Nos. + 1 Spare |  | Nos. | 3 | 24129 | 72387 | 9375 | 28125
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan - DOL Starter (1.1KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | Celing Suspended AHUs - DOL Starter (1KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | Celing Suspended AHUs - DOL Starter (0.8KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1.6 - 2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | Celing Suspended AHUs - DOL Starter (0.6KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1 - 1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-2F Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air handling unit - Y-∆ Starter (18.5 KW) - 01 Nos. |  | Nos. | 1 | 57085 | 57085 | 9375 | 9375
| MPCB TP 50, Iq 50kA - 01 Nos. | L&TMOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 70A Power contactor (Start, Delta & Main) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 70A Power contactor for VFD (I/P, O/P & Isolation ) - 03 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| OLR (20-33), Iq 50kA - 01 Nos. | L&T MN2 |  |  | 0 |  | 0
| ON-Delay (Y-∆) Timer - 01 Nos. | L&T GIC |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | CHW Air handling unit - DOL Starter (3 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW Air handling unit - DOL Starter (1.5 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | CHW Air handling unit - DOL Starter (1.3 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Air handling unit - DOL Starter (0.55 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1 - 1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 02 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C6. | THIRD FLOOR |  |  |  | 0 |  | 0
a. | Floor-3F-Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Air Handling Unit (EC Fan)- DOL Starter (2.2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Ceiling Suspended Unit (EC Fan)- DOL Starter (2.1 KW) - 02 Nos.+1 Spare |  | Nos. | 3 | 494929 | 1484787 | 9375 | 28125
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | Air Handling Unit (EC Fan)- DOL Starter (1.6 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabinet Fan (EC Fan)- DOL Starter (1.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | Air Handling Unit (EC Fan)- DOL Starter (1.2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | Ceiling Suspended Unit (EC Fan)- DOL Starter (1.2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | EA Cabinet Fan- DOL Starter (1.1KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | Air Handling Unit (Plug Fan)- DOL Starter (1 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | Ceiling Suspended Unit (Plug Fan)- DOL Starter (0.8 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-3F-Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air handling unit- VFD/Y-∆ Starter(10KW) - 01 Nos. |  | Nos. | 1 | 41784 | 41784 | 9375 | 9375
| MPCB TP 32 A, Iq 50kA - 01 Nos. | L&T MOG-H1M |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (star) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 50A Power contactor (Main & Delta) - 02 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| 50A Power contactor for VFD (I/P, O/P & Isolation) - 03 Nos. | L&T MNX 50 |  |  | 0 |  | 0
| ON-Delay Timer | L&T GIC |  |  | 0 |  | 0
| OLR (9-15A) Iq=50 kA - 01 Nos | L&T MN5 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. | Keycee |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | CHW Air handling unit - DOL Starter (5 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | Smoke spill Axial flow fan- DOL Starter (5 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabinet Fan (EC Fan)- DOL Starter (2.2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | EA Cabinet Fan (EC Fan)- DOL Starter (1.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan (EC Fan)- DOL Starter (0.55 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 09A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C7. | FOURTH FLOOR |  |  |  | 0 |  | 0
a. | Floor-4F Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Smoke spill Axial flow fan - DOL Starter (3 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Smoke spill Axial flow fan - DOL Starter (2.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW Air handling unit - DOL Starter (2.4 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | Ceiling Suspended Unit- DOL Starter (2.3 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Air handling unit - DOL Starter (1.8 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan- DOL Starter (1.5KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | Celing Suspended AHUs - DOL Starter (1.3KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | EA Cabinet Fan- DOL Starter (1.1KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | Celing Suspended AHUs - DOL Starter (0.8KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.1 | Celing Suspended AHUs - DOL Starter (0.6KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-4F Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Smoke spill Axial flow fan - DOL Starter (5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Smoke spill Axial flow fan - DOL Starter (2.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | EA Cabinet Fan - DOL Starter (2.2 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | EA Cabinet Fan - DOL Starter (1.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Air Handling Unit- DOL Starter (1.3KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan - DOL Starter (0.55 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C8. | FIFTH FLOOR |  |  |  | 0 |  | 0
a. | Floor-5F Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Smoke spill Axial flow fan - DOL Starter (4 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Smoke spill Axial flow fan- DOL Starter (3KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW PAC Unit- DOL Starter (1.9KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
1.4 | CHW Air handling unit- DOL Starter (1.8KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | EA Cabinet Fan- DOL Starter (1.5KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan- DOL Starter (1.1KW) - 02 Nos. + 1 Spare |  | Nos. | 3 | 24129 | 72387 | 9375 | 28125
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-5F Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | Smoke spill Axial flow fan - DOL Starter (5 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | Smoke spill Axial flow fan - DOL Starter (4 KW) - 01 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| 25A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | EA Cabinet Fan- DOL Starter (1.5 KW) - 1 Nos. |  | Nos. | 1 | 30014 | 30014 | 9375 | 9375
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| 12A Power contactor for VFD (I/P, O/P ) - 02 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| VFD/Bypass mode Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | CHW Ceiling suspended unit- DOL Starter (1.3 KW) - 1 Nos. + 1 Spare |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Ceiling suspended unit- DOL Starter (0.8KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | EA Cabinet Fan- DOL Starter (0.55 KW) - 1 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| Control MCB 1P 6A 10kA C Curve - 01 Nos. | L&T BB10060C |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 9 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm (Bus-bar Type) - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
C9. | SIXTH FLOOR |  |  |  | 0 |  | 0
a. | Floor-6F Panel (Left Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Air handling unit- DOL Starter (7.3 KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(11-16 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 6 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 4 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | CHW Air handling unit- DOL Starter (5.0 KW) - 08 Nos. |  | Nos. | 8 | 24129 | 193032 | 31250 | 250000
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | Smoke spill Axial flow fan- DOL Starter (5.0 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(9-13 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | CHW Ttreated fresh air unit- DOL Starter (4 KW) -01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(6.3-10 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 25A Power contactor (DOL) - 01 Nos. | L&T MNX 25 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | CHW Ceiling suspended unit- DOL Starter (1.9KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | Celing Suspended AHUs EC Fan)- DOL Starter (1.3KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | EA Cabinet Fan- DOL Starter (1.1KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | CHW Ceiling suspended unit- DOL Starter (0.8KW) - 04 Nos. |  | Nos. | 4 | 24129 | 96516 | 18750 | 75000
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 09A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
b. | Floor-6F Panel (Right Zone) |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1 | Starters (3ø) |  |  |  | 0 |  | 0
1.1 | CHW Ceiling suspended unit- DOL Starter (3.1 KW) - 01 Nos |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.2 | CHW Air handling unit- DOL Starter (3 KW) - 01 Nos |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.3 | CHW Air handling unit- DOL Starter (2.9 KW) - 01 Nos |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.4 | CHW Air handling unit- DOL Starter (2.4KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.5 | EA Cabinet Fan- DOL Starter (2.2KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.6 | CHW Air handling unit- DOL Starter (1.7 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.7 | CHW Air handling unit- DOL Starter (1.6 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(4-6.3 A), Iq 50kA - 01 Nos. | L&T MOG H1 |  |  | 0 |  | 0
| 22A Power contactor (DOL) - 01 Nos. | L&T MNX 22 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.8 | EA Cabinet Fan- DOL Starter (1.5 KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.9 | CHW Ceiling suspended unit- DOL Starter (1.1KW) - 05 Nos. |  | Nos. | 5 | 24129 | 120645 | 18750 | 93750
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.1 | CHW Ceiling suspended unit- DOL Starter (1.0KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 6250 | 6250
| MPCB TP(2.5-4 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 12A Power contactor (DOL) - 01 Nos. | L&T MNX 12 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.11 | CHW Ceiling suspended unit- DOL Starter (0.8KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 09A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.12 | CHW Ceiling suspended unit- DOL Starter (0.7KW) - 02 Nos. |  | Nos. | 2 | 24129 | 48258 | 9375 | 18750
| MPCB TP(1.6-2.5 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 09A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
1.13 | EA Cabinet Fan- DOL Starter (0.55KW) - 01 Nos. |  | Nos. | 1 | 24129 | 24129 | 9375 | 9375
| MPCB TP(1-1.6 A), Iq 50kA - 01 Nos. | L&T MOG S1 |  |  | 0 |  | 0
| 9A Power contactor (DOL) - 01 Nos. | L&T MNX 09 |  |  | 0 |  | 0
| ON/Off/Trip Indicator, Red, Green & Amber, 230VAC - 03 Nos. |  |  |  | 0 |  | 0
| Auto/Manual Selector Switch - 01 Nos. |  |  |  | 0 |  | 0
| Start and Stop (Mashroom Head) Push Button - 1 Nos. each |  |  |  | 0 |  | 0
| Miniature Relay (4NO+4NC) , 230 VAC - 01 Nos. |  |  |  | 0 |  | 0
| Power Terminal 4 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Control Terminal, 2.5 sq.mm - 8 Nos. |  |  |  | 0 |  | 0
| Power Wire - 2.5 sq mm |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
D. | CABLES |  |  |  | 0 |  | 0
1.1 | Supply & laying testing and commissioning of following sizes of PVC insulated PVC sheathed armoured copper conductor/Aluminum cable of 1.1 KV grade on existing cable tray / surface including clamps, ties etc. complete as required. |  |  |  | 0 |  | 0
1.1.1 | 3.5C x 300 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 120 | 2258 | 270960 | 150 | 18000
1.1.2 | 3.5C x 240 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 48 | 1853 | 88944 | 150 | 7200
1.1.3 | 3.5C x 185 sq.mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 140 | 1449 | 202860 | 100 | 14000
1.1.4 | 3.5C x 120 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 16 | 983 | 15728 | 100 | 1600
1.1.5 | 3.5C x 70 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 16 | 650 | 10400 | 100 | 1600
1.1.6 | 3.5C x 50 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 80 | 488 | 39040 | 100 | 8000
1.1.7 | 3.5C x 35 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 80 | 371 | 29680 | 100 | 8000
1.1.8 | 3.5C x 16 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 32 | 185 | 5920 | 50 | 1600
1.1.9 | 4C x 16 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | RMT. | 32 | 268 | 8576 | 50 | 1600
1.1.10 | 4C x 10 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 32 | 865 | 27680 | 50 | 1600
1.1.11 | 4C x 6 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 0 | 538 | 0 | 50 | 0
1.1.12 | 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 192 | 388 | 74496 | 50 | 9600
1.1.13 | 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 224 | 283 | 63392 | 50 | 11200
1.1.14 | 4C x 1.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 704 | 198 | 139392 | 50 | 35200
1.1.15 | 4C x 1sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | RMT. | 320 | 137 | 43840 | 50 | 16000
1.1.16 | 3C x 6sq.mm X 1 runs XLPE Insulated Copper multi-strand armoured cable |  | RMT. | 64 | 423 | 27072 | 50 | 3200
1.1.17 | 3C x 4sq.mm X 1 runs XLPE Insulated Copper multi-strand armoured cable |  | RMT. | 400 | 313 | 125200 | 50 | 20000
1.1.18 | 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | RMT. | 464 | 231 | 107184 | 50 | 23200
1.1.19 | 3C x 1.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | RMT. | 1312 | 166 | 217792 | 50 | 65600
1.1.20 | 3C x 1 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | RMT. | 5264 | 124 | 652736 | 50 | 263200
[5 empty] | 0 |  | 0
1.2. | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 |  | 0
1.2.1 | 3.5C x 300 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 24 | 2349 | 56376 | 75 | 1800
1.2.2 | 3.5C x 240 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 6 | 1944 | 11664 | 75 | 450
1.2.3 | 3.5C x 185 sq.mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 4 | 1475 | 5900 | 75 | 300
1.2.4 | 3.5C x 120 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 2 | 1003 | 2006 | 75 | 150
1.2.5 | 3.5C x 70 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 2 | 644 | 1288 | 75 | 150
1.2.6 | 3.5C x 50 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 10 | 481 | 4810 | 38 | 380
1.2.7 | 3.5C x 35 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 10 | 355 | 3550 | 38 | 380
1.2.8 | 3.5C x 16 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 4 | 169 | 676 | 38 | 152
1.2.9 | 4C x 16 sq. mm x 1 runs XLPE Insulated FRLS aluminium multistrad armoured cable |  | Nos. | 4 | 252 | 1008 | 38 | 152
1.2.10 | 4C x 10 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 4 | 849 | 3396 | 38 | 152
1.2.11 | 4C x 6 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 0 | 523 | 0 | 38 | 0
1.2.12 | 4C x 4 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 24 | 372 | 8928 | 38 | 912
1.2.13 | 4C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 28 | 267 | 7476 | 38 | 1064
1.2.14 | 4C x 1.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 88 | 183 | 16104 | 38 | 3344
1.2.15 | 4C x 1sq. mm x 1 runs XLPE Insulated FRLS Copper multi-strand armoured cable |  | Nos. | 40 | 121 | 4840 | 38 | 1520
1.2.16 | 3C x 6sq.mm X 1 runs XLPE Insulated Copper multi-strand armoured cable |  | Nos. | 8 | 408 | 3264 | 38 | 304
1.2.17 | 3C x 4sq.mm X 1 runs XLPE Insulated Copper multi-strand armoured cable |  | Nos. | 50 | 298 | 14900 | 38 | 1900
1.2.18 | 3C x 2.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | Nos. | 58 | 215 | 12470 | 38 | 2204
1.2.19 | 3C x 1.5 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | Nos. | 164 | 150 | 24600 | 38 | 6232
1.2.20 | 3C x 1 sq. mm x 1 runs XLPE Insulated FRLS Copper multistrand armoured cable |  | Nos. | 658 | 108 | 71064 | 38 | 25004
[5 empty] | 0 |  | 0
1.3 | Supply, Fabricating and installation following size of perforated GI cable trays 1.2 mm thick including horizontal and vertical GI bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders and including painting etc. complete as required & approved by the Engineer In Charge. |  |  |  | 0 |  | 0
1.3.1 | 600 mm Width x 50mm. Depth x 1.6mm. Thickness |  | RMT. | 200 | 1626 | 325200 | 250 | 50000
1.3.2 | 450 mm Width x 50mm. Depth x 1.6mm. Thickness |  | RMT. | 500 | 1034 | 517000 | 250 | 125000
1.3.3 | 300 mm. Width x 40mm. Depth x 1.6mm. Thickness. |  | RMT. | 800 | 724 | 579200 | 250 | 200000
1.3.4 | 150 mm. Width x 40mm. Depth x 1.6mm. Thickness. |  | RMT. | 1200 | 449 | 538800 | 250 | 300000
1.3.5 | 100 mm. Width x 40mm. Depth x 1.6mm. Thickness. |  | RMT. | 2500 | 358 | 895000 | 250 | 625000
[5 empty] | 0 |  | 0
1.4 | Supply and fixing of following bare GI tapes / SWG wires including all necessary fixing accessories and effecting connections as per specifications. |  |  |  | 0 |  | 0
1.4.1 | 25 mm X 6 mm GI Strip |  | RMT. | 120 | 144 | 17280 | 38 | 4560
1.4.2 | 6 mm Dia Copper Wire |  | RMT. | 150 | 273 | 40950 | 25 | 3750
1.4.3 | 4 mm Dia Copper Wire |  | RMT. | 1500 | 182 | 273000 | 25 | 37500
1.4.4 | 3 mm Dia Copper Wire |  | RMT. | 7800 | 117 | 912600 | 25 | 195000
| SUM ELECTRICAL WORKS EXCLUSIVE OF GST |  |  |  |  | 33759695 |  | 10529010

## 4.AHU SCHEDULE
AHU SCHEDULE
[5 empty] | Fan Section | Selected Equipment |  |  |  |  | Filter Section
S.No | Floor Level | Equipment Type | Space Name | TAG | Fan Type | Total Cooling load | Supply Air Quantity |  | External Static | Qty | Filter Bank-1 | Filter Bank-2 | Terminal
[6 empty] | TR | CMH | CFM | Pa |  | Pre-Filter | Fine-Filter | Super Fine Filter
1 | LB | FMU | Linear Acclerator room | #N/A | EC Fan | 4 | 3800 | 2242 | 250 | 1 | MERV 8 | MERV 13
2 | LB | CSU | Brachy Therapy | #N/A | EC Fan | 2 | 1700 | 1003 | 250 | 1 | MERV 8
3 | LB | CSU | PET CT | #N/A | EC Fan | 4 | 3700 | 2183 | 250 | 1 | MERV 8
4 | LB | CSU | SPECT | #N/A | EC Fan | 4 | 4200 | 2478 | 250 | 1 | MERV 8
5 | LB | CSU | PETCT Technical room | #N/A | EC Fan | 1 | 550 | 325 | 250 | 1 | MERV 8
6 | LB | CSU | UPS Room (LA,HDR,PETCT & SPECT) | #N/A | EC Fan | 5 | 5000 | 2950 | 250 | 1 | MERV 8
7 | LB | CSU | Opeartion Theatre | #N/A | EC Fan | 5 | 6200 | 3658 | 250 | 1 | MERV 8 | MERV 13
8 | LB | CSU | Corridor & Waiting area - 118 Nos | #N/A | EC Fan | 4 | 3300 | 1947 | 250 | 1 | MERV 8
9 | UB | CSU | Central UPS Room | #N/A | EC Fan | 5 | 2800 | 1652 | 250 | 2 | MERV 8
10 | GF | CSU | Service Lobby & Waiting area | #N/A | EC Fan | 9 | 8400 | 4956 | 350 | 1 | MERV 8 | MERV 10
11 | GF | FMU | Casualty | #N/A | EC Fan | 10 | 7100 | 4189 | 250 | 1 | MERV 8
12 | GF | CSU | Pediatric & OBG Ward | #N/A | EC Fan | 5 | 3300 | 1947 | 250 | 1 | MERV 8
13 | GF | CSU | Admisssion and Discharge waiting | #N/A | EC Fan | 11 | 7600 | 4484 | 250 | 1 | MERV 8 | MERV 10
14 | GF | CSU | Cubicle | #N/A | EC Fan | 4 | 3400 | 2006 | 250 | 1 | MERV 8
15 | GF | CSU | CT Scan | #N/A | EC Fan | 6 | 7400 | 4366 | 250 | 1 | MERV 8
16 | GF | CSU | Snack bar | #N/A | EC Fan | 18 | 11700 | 6903 | 250 | 1 | MERV 8
17 | GF | CSU | Pharmacy | #N/A | EC Fan | 4 | 4200 | 2478 | 250 | 1 | MERV 8
18 | GF | FMU | OPG OPD Area - 116 Nos and Pediatric OPD Area - 78 Nos & Reception waiting area | #N/A | EC Fan+ | 42 | 44300 | 26137 | 350 | 1 | MERV 8 | MERV 10
19 | 1F | FMU | Ultrasound waiting area - 106+78+82 Nos | #N/A | EC Fan+ | 41 | 33000 | 19470 | 350 | 1 | MERV 8 | MERV 10
20 | 1F | CSU | CT Scan | #N/A | EC Fan | 6 | 6400 | 3776 | 250 | 1 | MERV 8
21 | 1F | CSU | Recovery room | #N/A | EC Fan | 2 | 2300 | 1357 | 250 | 1 | MERV 8
22 | 1F | CSU | MRI Scan | #N/A | EC Fan | 4 | 4500 | 2655 | 250 | 1 | MERV 8
23 | 1F | CSU | MRI Scan | #N/A | EC Fan | 3 | 2800 | 1652 | 250 | 1 | MERV 8
24 | 1F | CSU | CT Scan Future | #N/A | EC Fan | 5 | 5900 | 3481 | 250 | 1 | MERV 8
25 | 1F | FMU | Waiting area + 49 consultants | #N/A | EC Fan+ | 62 | 50700 | 29913 | 350 | 1 | MERV 8 | MERV 10
26 | 1F | CSU | Registration | #N/A | EC Fan | 5 | 4200 | 2478 | 200 | 1 | MERV 8
27 | 1F | CSU | Main Entry (Trible Height) | #N/A | EC Fan | 7 | 9400 | 5546 | 250 | 1 | MERV 8
28 | 2F | CSU | Isolation | #N/A | EC Fan | 4 | 3700 | 2183 | 250 | 1 | MERV 8 | - | -
29 | 2F | CSU | Chemoward | #N/A | EC Fan | 3 | 2700 | 1593 | 200 | 1 | MERV 8 | - | -
30 | 2F | CSU | Dialysis | #N/A | EC Fan | 7 | 6300 | 3717 | 200 | 1 | MERV 8 | - | -
31 | 2F | CSU | ICU | #N/A | EC Fan | 5 | 3800 | 2242 | 250 | 1 | MERV 8 | MERV 13 | -
32 | 2F | FMU | Dining | #N/A | EC Fan | 14 | 12300 | 7257 | 200 | 1 | MERV 8 | - | -
33 | 2F | FMU | Waiting area - 136+78 No+Consultants | #N/A | EC Fan+ | 57 | 50700 | 29913 | 350 | 1 | MERV 8 | MERV 10 | -
34 | 2F | FMU | OT | #N/A | EC Fan | 5 | 5500 | 3245 | 350 | 1 | MERV 8 | MERV 13 | H13 HEPA
35 | 2F | CSU | Daycare | #N/A | EC Fan | 4 | 4500 | 2655 | 250 | 1 | MERV 8 | - | -
36 | 2F | CSU | Registration | #N/A | EC Fan | 7 | 3500 | 2065 | 200 | 1 | MERV 8 | - | -
37 | 2F | CSU | Corridor | #N/A | EC Fan | 2 | 1400 | 826 | 250 | 1 | MERV 8 | - | -
38 | 3F | CSU | Corridor | #N/A | EC Fan | 2 | 2200 | 1298 | 250 | 1 | MERV 8 | - | -
39 | 3F | CSU | ICU | #N/A | EC Fan | 3 | 4100 | 2419 | 150 | 1 | MERV 8 | MERV 13 | -
40 | 3F | CSU | CICU | #N/A | EC Fan | 8 | 8000 | 4720 | 250 | 1 | MERV 8 | MERV 13
41 | 3F | FMU | Cath lab-1 and UPS & Technical room | #N/A | EC Fan | 5 | 6300 | 3717 | 250 | 1 | MERV 8 | MERV 13
42 | 3F | FMU | Cath lab-2 and UPS & Technical room | #N/A | EC Fan | 4 | 4500 | 2655 | 250 | 1 | MERV 8 | MERV 13
43 | 3F | FMU | Pre & Post OP | #N/A | EC Fan | 2 | 2600 | 1534 | 250 | 1 | MERV 8 | MERV 13
44 | 3F | CSU | MICU-1 | #N/A | EC Fan | 7 | 7800 | 4602 | 250 | 1 | MERV 8 | MERV 13
45 | 3F | FMU | Future Expansion | #N/A | EC Fan | 6 | 6000 | 3540 | 250 | 1 | MERV 8
46 | 3F | FMU | Waiting area | #N/A | EC Fan | 14 | 11100 | 6549 | 250 | 1 | MERV 8 | MERV 10
47 | 3F | FMU | Blood Bank | #N/A | EC Fan | 8 | 7500 | 4425 | 250 | 1 | MERV 8
48 | 3F | CSU | Lift lobby | #N/A | EC Fan | 2 | 2000 | 1180 | 250 | 1 | MERV 8
49 | 4F | FMU | Opeartion Theatre -1 | #N/A | EC Fan | 7 | 7600 | 4484 | 350 | 1 | MERV 8 | MERV 13 | H13 HEPA
50 | 4F | FMU | Opeartion Theatre -2 | #N/A | EC Fan | 6 | 6100 | 3599 | 350 | 1 | MERV 8 | MERV 13 | H13 HEPA
51 | 4F | CSU | NICU & PICU Waiting area | #N/A | EC Fan | 6 | 6500 | 3835 | 250 | 1 | MERV 8 | MERV 10
52 | 4F | CSU | Pre & Post Operative | #N/A | EC Fan | 1 | 800 | 472 | 150 | 1 | MERV 8 | MERV 13
53 | 4F | CSU | PICU | #N/A | EC Fan | 6 | 6500 | 3835 | 250 | 1 | MERV 8 | MERV 13
54 | 4F | FMU | NICU | #N/A | EC Fan | 7 | 5300 | 3127 | 250 | 1 | MERV 8 | MERV 13
55 | 4F | FMU | Corridor | #N/A | EC Fan | 3 | 3800 | 2242 | 250 | 1 | MERV 8
56 | 4F | CSU | Nurse station & Corridor | #N/A | EC Fan | 2 | 2700 | 1593 | 250 | 1 | MERV 8
57 | 5F | CSU | General ward - Male | #N/A | EC Fan | 3 | 2600 | 1534 | 250 | 1 | MERV 8
58 | 5F | CSU | General ward - Female | #N/A | EC Fan | 3 | 1600 | 944 | 250 | 1 | MERV 8
59 | 5F | FMU | Corridor | #N/A | EC Fan | 4 | 4800 | 2832 | 250 | 1 | MERV 8
60 | 5F | CSU | Waiting area | #N/A | EC Fan | 5 | 4200 | 2478 | 250 | 1 | MERV 8 | MERV 10
61 | 6F | FMU | Opeartion Theatre - 1 | #N/A | EC Fan | 18 | 24200 | 14278 | 350 | 1 | MERV 8 | MERV 13 | H13 HEPA
62 | 6F | FMU | Opeartion Theatre - 2 | #N/A | EC Fan | 18 | 24200 | 14278 | 350 | 1 | MERV 8 | MERV 13 | H13 HEPA
63 | 6F | FMU | Opeartion Theatre - 3-6 | #N/A | EC Fan | 6 | 11000 | 6490 | 350 | 4 | MERV 8 | MERV 13 | H13 HEPA
64 | 6F | FMU | Opeartion Theatre - 7-10 | #N/A | EC Fan | 6 | 11000 | 6490 | 350 | 4 | MERV 8 | MERV 13 | H13 HEPA
65 | 6F | CSU | Transplant ICU | #N/A | EC Fan | 2 | 1500 | 885 | 200 | 1 | MERV 8 | MERV 13
66 | 6F | CSU | Waiting area - 186 Nos | #N/A | EC Fan | 16 | 12000 | 7080 | 250 | 1 | MERV 8 | MERV 10
67 | 6F | FMU | Post- OP | #N/A | EC Fan | 7 | 6000 | 3540 | 350 | 1 | MERV 8 | MERV 13
68 | 6F | FMU | Pre-OP | #N/A | EC Fan | 7 | 6900 | 4071 | 350 | 1 | MERV 8 | MERV 13
69 | 6F | FMU | S.I.C.U-1 | #N/A | EC Fan | 11 | 9300 | 5487 | 350 | 1 | MERV 8 | MERV 13
70 | 6F | FMU | S.I.C.U-3 | #N/A | EC Fan | 9 | 10000 | 5900 | 350 | 1 | MERV 8 | MERV 13
71 | 6F | CSU | BMT Room | #N/A | EC Fan | 3 | 4000 | 2360 | 150 | 6 | MERV 8 | MERV 13
72 | 6F | CSU | NEG BMT Room | #N/A | EC Fan | 2 | 2500 | 1475 | 350 | 1 | MERV 8 | MERV 13
73 | 6F | FMU | Corridor | #N/A | EC Fan | 6 | 5000 | 2950 | 250 | 1 | MERV 8
74 | 6F | CSU | Corridor | #N/A | EC Fan | 5 | 4500 | 2655 | 250 | 1 | MERV 8
75 | Terrace | CSU | ICU Waiting Area | #N/A | EC Fan | 13 | 10600 | 6254 | 250 | 1 | MERV 8
76 | Terrace | CSU | C.Dining Area | #N/A | EC Fan | 7 | 5200 | 3068 | 250 | 1 | MERV 8
77 | Terrace | CSU | Dr.and Staff Dining area | #N/A | EC Fan | 16 | 15500 | 9145 | 250 | 1 | MERV 8
78 | Terrace | CSU | CSSD | #N/A | EC Fan | 14 | 14600 | 8614 | 250 | 1 | MERV 8
90

## 5.CRITICAL SPARE AHU
AHU SCHEDULE
CRITICAL SPARE AHU DETAILS
|  |  |  | Fan Section | Selected Equipment |  | Filter Section
S.No | Floor Level | Equipment Type | Space Name | Fan Type | Total Cooling load | Supply Air Quantity | Filter Bank-1 | Filter Bank-2 | Filter Bank-3
[5 empty] | TR | CMH | Pre-Filter | Fine-Filter | Super Fine Filter
1 | LB | CSU | Opeartion Theatre | EC Fan | 5 | 6200 | MERV 8 | MERV 13
2 | 2F | FMU | ICU | EC Fan | 5 | 3800 | MERV 8 | MERV 13 | -
3 | 2F | FMU | OT | EC Fan | 4 | 5600 | MERV 8 | MERV 13 | H13 HEPA
4 | 3F | CSU | ICU | EC Fan | 3 | 4100 | MERV 8 | MERV 13 | -
5 | 3F | CSU | CICU | EC Fan | 8 | 8000 | MERV 8 | MERV 13
6 | 3F | FMU | Cath lab-1 and UPS & Technical room | EC Fan | 4 | 5000 | MERV 8 | MERV 13
7 | 3F | FMU | Pre & Post OP | EC Fan | 2 | 1600 | MERV 8 | MERV 13
8 | 3F | FMU | MICU-1 | EC Fan | 7 | 7800 | MERV 8 | MERV 13
9 | 4F | FMU | Opeartion Theatre -1 | EC Fan | 6 | 7600 | MERV 8 | MERV 13 | H13 HEPA
10 | 4F | FMU | Opeartion Theatre -2 | EC Fan | 5 | 6100 | MERV 8 | MERV 13 | H13 HEPA
11 | 4F | CSU | Pre & Post Operative | EC Fan | 1 | 800 | MERV 8 | MERV 13
12 | 4F | CSU | PICU | EC Fan | 6 | 6500 | MERV 8 | MERV 13
13 | 4F | FMU | NICU | EC Fan | 7 | 5300 | MERV 8 | MERV 13
14 | 6F | FMU | Opeartion Theatre - 1 | EC Fan | 18 | 24200 | MERV 8 | MERV 13 | H13 HEPA
15 | 6F | FMU | Opeartion Theatre - 2 | EC Fan | 8 | 11000 | MERV 8 | MERV 13 | H13 HEPA
16 | 6F | FMU | Post- OP | EC Fan | 7 | 5800 | MERV 8 | MERV 13
17 | 6F | FMU | Pre-OP | EC Fan | 7 | 6900 | MERV 8 | MERV 13
18 | 6F | FMU | S.I.C.U-1 | EC Fan | 11 | 9300 | MERV 8 | MERV 13
19 | 6F | FMU | S.I.C.U-3 | EC Fan | 7 | 10000 | MERV 8 | MERV 13
20 | 6F | CSU | BMT Room | EC Fan | 3 | 4000 | MERV 8 | MERV 13

## 6.WC Chiller Annexure C
Chiller Comprehensive AMC scope - Annexure C
S.No | List of Actions | Schedule
|  | General | Once in 2 months | Once in 6 months | Once in 2 years
1 | Overhauling of chiller equipments,components and replacing of faulty / non performing components | As required to maintain UP time commitment of 99.50%, including stand-by
2 | The manufacturer shall depute Engineers & technicians to attend chiller breakdowns, whenever received call from clients | ü
3 | Attending clients complaint of failure / Break downs of electrical power, controls of chiller,replacing faulting components at free of cost, and resolving to clients satisfaction | 2 to 4 hours, within registering of complaint call
4 | Attending cleints complaint of failure / Break downs of minor mechanical components of chiller, replacing faulting components at free of cost, and resolving to clients satisfaction | 6 to 24 hours, within registering of complaint call
5 | Attending cleints complaint of faiure / Break downs of major mechanical components of chiller (except compressors), replacing faulting components at free of cost, and resolving to clients satisfaction | 24 to 72 hours, within registering of complaint call
6 | Attending cleints complaint of faiure / Break downs of compressors, replacing faulting components at free of cost, and resolving to clients satisfaction | with 7 days (including holidays)
7 | Manufacturer shall perform the regular maintenance as per their standard practice and report to clients if any development required. |  | ü
8 | Health checkup shall be done for entire chiller components |  |  | ü
9 | Monitoring compressor operation and its accessories |  | ü
10 | If any leakages in refrigeration system, that would be found and rectified. |  | ü
11 | Compressor oil and bearing shall be replaced. |  |  |  | ü
12 | The manufacturer shall visit the site for part load evaluation as per factory performance |  |  | ü
13 | Refrigeration control system shall be checked and adjusted. |  | ü
14 | Scale formation in the condenser coil shall be cleaned. |  |  | ü
15 | lubricating motor bearings and fans |  | ü
16 | Physical inspection for compresor oil shall be carried out |  | ü
17 | Monitoring of micro preccessor controller. If any replacement/modification required that would be done by manufacturer. |  | ü

## 7.WC Chiller Annexure A
ANNEXURE - A
WATER-COOLED SCREW CHILLER - PRODUCT DATA
# | PARAMETER | DESCRIPTION
1 | GENERAL:
1.1 | Make, Model & Origin:
1.2 | Refrigerant Used
1.3 | Capacity - TR
1.4 | No. of Compressors / Machine
1.5 | No. of Condenser Coil / Machine
1.6 | No. of Chillers / Machine
1.7 | No. of Circuits
1.8 | Describe Configuration of Circuits
1.9 | Operating Condensing Temperature - deg C
1.1 | Operating Suction temperature - deg C
1.11 | Evaporator Leaving Water Temperature - deg C
1.12 | Overall dimensions including stand (mm)
1.13 | Operating Weight - kg
1.14 | Operating Charge – kg
1.15 | Minimum clearance required from adjacent Structures - m
1.16 | Minimum clearance required between two Machines – m
1.17 | Whether any platform or pedestal required for Installation? If so, furnish details.
1.18 | Noise level at a distance of 1 m from the machine at intervals of 1 m along the perimeter – dB(A)
1.19 | Noise level when all the machines are working – dB(A)
1.2 | Casing:
1.20.1 | Material
1.20.2 | Thickness of material
1.20.3 | Method and details of construction
1.20.4 | Nature and joints used - whether folded, Welded, bolted, etc.,
1.20.5 | What is the finish, i.e., hot dip galvanized, Corrosion resistant, etc.,
1.20.6 | Whether factory fabricated?
1.21 | Cable size required :
1.22 | Isolator Rating required :
1.23 | Separate isolator to receive Un-interrupted power supply for controller required? Please specify the rating.
1.24 | Separate isolator to receive Un-interrupted power supply for oil heater required? Please specify the rating.
2 | SCREW COMPRESSOR – MOTOR UNIT
2.1 | Quantity per Machine
2.2 | Make
2.3 | Model
2.4 | Type
2.5 | Whether hermetic or semi-hermetic?
2.6 | Whether Vertical or Horizontal Cylinder?
2.7 | Capacity at operating conditions - TR
2.8 | Power Consumed – kW
2.9 | Drive losses – kW
2.1 | Motor efficiency - %
2.11 | In put kW
2.12 | kW / TR
# | PARAMETER | DESCRIPTION
2.13 | No. of lobes in male rotor
2.14 | Male rotor dia. – mm
2.15 | No. of lobes in female rotor
2.16 | Female rotor dia. – mm
2.17 | Which is the Driving Rotor?
2.18 | Material of the Rotor
2.19 | Type of Bearings
2.2 | Volume Ratio
2.21 | Is Volume Ratio Fixed or Variable?
2.22 | How are the following achieved?
2.22.1 | Cooling
2.22.2 | Sealing
2.22.3 | Bearing Lubrication
2.22.4 | (Furnish Description with Schematic Diagram)
2.23 | If Oil is used, furnish following information
2.23.1 | Oil Separator: Dia. (mm)
2.23.2 | Oil Separator: Length (mm)
2.23.3 | Oil Separator: Oil carryover - mg/kg
2.23.4 | Oil Separator: Constructional Details
2.23.5 | Oil Cooler: Oil injection temperature - °C
2.23.6 | Oil Cooler: Is an external oil cooler used? If yes, furnish details
2.23.7 | Oil Cooler: Is an oil pump used? If yes, furnish details
2.23.8 | Oil Cooler: Method of oil cooling
2.24 | Describe Capacity Control Mechanism Provided (Attach Literature)
2.25 | Minimum capacity at which machine can operate
2.26 | Is compressor fully unloaded at start, if not indicate % unloading
2.27 | Motor
2.28 | Motor kW, rpm
2.29 | Motor Rated Current - Amps
2.3 | Motor Type of Starter Used
2.31 | Motor Starting Current – Amps
2.32 | Motor Whether SPDP or TEFC?
2.33 | Motor Make
2.34 | Motor Model / Frame designation
3 | WATER COOLED CONDENSER:
3.1 | Type of heat exchanger
3.2 | Shell material
3.3 | Tube material
3.4 | Condenser Pressure Drop:
3.5 | Selected Condenser water inlet temp, 0C
3.6 | Selected Condenser water outlet temp, 0C
3.7 | Selected Condenser water flow rate, l/s
3.8 | Minimum flow rate, %
3.9 | Tube OD – mm
3.1 | No. of tubes
3.11 | Length of tubes – mm
3.12 | Condensing temperature - deg C
# | PARAMETER | DESCRIPTION
3.13 | Whether any sub-cooling circuit provided and if so, indicate the deg C of sub-cooling available
3.14 | Pressure drop across the coil - mm wg
3.15 | Operating charge – kg
3.16 | Maximum charge – kg
3.17 | Is a receiver required? If so, whether receiver included.
3.18 | Test pressure – kg
3.19 | Method of test
4 | CHILLER:
4.1 | Type of chiller (dry-ex or flooded)
4.2 | Shell OD – mm
4.3 | Overall length – mm
4.4 | Overall weight – kg
4.5 | Number of tubes
4.6 | Tube OD – mm
4.7 | Nature of tubes (whether integrally finned or Whether tubes carry inserts)
4.8 | Length of tube between tube sheets
4.9 | Material of tube
4.1 | Material of shell
4.11 | Water side surface area – sq.m
4.12 | Refrigerant side surface area – sq.m
4.13 | Minimum operating charge of refrigerant – kg
4.14 | Water Flow rate – l/m
4.15 | Leaving water temperature – deg C
4.16 | Entering water temperature - deg C
4.17 | Refrigerant temperature - deg C
4.18 | Leaving temperature difference - deg C
4.19 | No. of passes
4.2 | Tube velocity – m/s
4.21 | Pressure drop – kg/sq.cm
4.22 | Design refrigerant approach temperature - deg C
5 | CONTROL PANEL
5.1 | How Many Chillers can it Handle?
5.2 | Is all the parameters, which are possible to view in the graphic screen mounted on chiller, are possible to view & modify from remote location?
5.3 | If yes, has it been included in the offer?
5.4 | Is necessary hardware & software required for integration included in the offer?
5.5 | Is quoted controller possible to operate primary chilled water pump sets, cooling towers & condenser water pump sets?
6 | UNIT MOUNTED STARTER
6.1 | Is unit mounted starters mentioned in the specs included in the offer?
6.2 | Is additional features like circuit breakers and mechanical non-fused disconnects are included in the offer?
6.3 | Make of VFD
6.4 | Is main isolator with extended handle considered in the offer?
7 | ARI / Eurovent Certification (Yes / No)
8 | SCOPE OF SUPPLY:
8.1 | Chiller
8.2 | Cooler Insulation
8.3 | Water flow switch for Evaporator & Condenser
8.4 | VFD
# | PARAMETER | DESCRIPTION
8.4 | BMS Hardware & Software
8.5 | Flow Switches
8.6 | Refrigerant & Oil
8.7 | Vibration Isolation
8.8 | Service Isolation Valve
8.9 | Standard Warranty (Years)

## 8.WC Chiller Annexure B
ANNEXURE – B
WATER-COOLED CHILLER - PERFORMANCE DATA (ikW/Tr)
CONDENSER WATER INLET TEMPERATURE (DEG C)
|  | 33 | 30 | 28 | 26 | 24 | 22 | 22
% OF LOAD | 100%
90%
80%
70%
60%
50%
40%
30%
20%
Cooler F.F.A. 0.018 (m² · K/ kW)
Condenser F.F.A. 0.044 (m² · K/ kW)

## 9.VENT FAN ANNEXURE
ANNEXURE - C
VENTILATION FAN TECHINICAL DATASHEET SUBMITTAL FORMAT
A | GENERAL | UNIT | VALUE
1 | Unit Tag
2 | Unit make
3 | Unit Model
4 | Fan Type
5 | Air Quantity | m³/h
6 | Total Static Pressure | Pa
7 | External Static Pressure | Pa
8 | Dimension (W x D x H) | mm
9 | Operating Weight | kg
10 | Smoke Rating | (Y/N)
B | FAN DATA | UNIT
11 | Air Volume | m³/h
12 | Fan Class
13 | Fan Diameter | mm
14 | Fan outlet velocity | m/s
15 | Static Pressure | Pa
16 | Velocity Pressure | Pa
17 | Fan Static Efficiency | %
18 | Fan Total Efficiency | %
19 | Fan Speed (Rated) | RPM
20 | Fan Speed (Maximum) | RPM
21 | Fan absorbed Power | kW
22 | Fan motor rating | kW
23 | Inspection Port | (Y/N)
24 | Anti-vibration mount type
25 | Sound Pressure Level @ 1.5 m | dB(A)
26 | Maximum Temperature rating for continuous operation | °C
C | MOTOR | UNIT
27 | Frame size | mm
28 | Motor kW | kW
29 | Enclosure Class
30 | Efficiency | %
31 | Number of Poles | Nos
32 | Motor Speed | RPM
33 | Power Supply | V-Ph-Hz
34 | Insulation Class
35 | Current (No Load) | Amp
36 | Current (Full Load) | Amp
37 | Current (Locked Rotor) | Amp
D | FAN MATERIAL | UNIT
38 | Outer Casing material
39 | Outer Casing thickness | mm
E | FILTER | UNIT
40 | Type
41 | Filter Grade
42 | Filter Media
43 | Frame Material
44 | Efficiency | %
45 | Clean Air Pressure Drop | Pa
46 | Mean Air Pressure Drop | Pa
47 | Dirty Air Pressure Drop | Pa
48 | Size (W X D X H) | mm
49 | Quantity | Nos
F | ELECTRICAL DETAILS
50 | Electrical Cable Specification
51 | Electrical Breaker Specification
52 | Communication Cable Specification
G | SUBMITTALS | UNIT
53 | Fan Catalogue
54 | Fan Performance Curve
55 | GA Drawing
56 | AMCA Certification for fan | (Y/N)
57 | High Temperature performance Certification for fan | (Y/N)
Note: Duplicate this format for more than one fan.

## 10.VRF ODU ANNEXURE - A
VRF ODU ANNEXURE
ANNEXURE - A
S.No | PARAMETERS | Outdoor unit 1 | Outdoor unit 2
1 | ODU TAG
2 | Nominal Capacity (HP)
3 | Specify Room wet bulb temperature in 0C @ nominal capacity
4 | Specify Room wet bulb temperature cosidered, in 0C @ actual capacity
5 | Specify capacity correction factor for change in room wet bulb temperature
6 | Specify outdoor dry bulb temperature in 0C @ nominal capacity
7 | Specify outdoor dry bulb temperature considered, in 0C @ actual capacity
8 | Specify capacity correction factor for change in outdoor dry bulb temperature
9 | Specify horizontal & vertical distance between indoor to outdoor units @ nominal capacity (meter)
10 | Specify horizontal distance between indoor to outdoor units @ actual capacity
11 | Specify capacity correction factor for change in horizontal distance between indoor to outdoor units
12 | Specify indoor unit / outdoor unit connectivity ration (diversity) @ nominal capacity
13 | Specify indoor unit / outdoor unit connectivity ration (diversity) @ actual capacity
14 | Specify capacity correction factor for change in indoor unit / outdoor unit connectivity ration (diversity)
15 | Total capacity correction factor | 0% | 0%
16 | Total capacity correction in HP | 0 | 0
17 | Actual Capacity(HP) | 0 | 0
18 | Actual Capacity(TR) | 0 | 0
19 | Required Capacity(TR)
20 | Proposed Outdoor Unit Model No

## 11.VRF ODU ANNEXURE - B
ANNEXURE - B
VRF OUTDOOR UNIT TECHNICAL DATA SHEET
1 | GENERAL | UNIT | DATA
1.1 | Make and Origin
1.2 | Model
1.3 | Capacities of each module & grouping
2 | CAPACITIES:
2.1 | Cooling Capacity | TR
2.2 | Cooling Input Power | kW
3 | Cooling Mode - Rated Conditions
3.1 | Indoor : 24°C DBT, 55% RH
3.2 | Outdoor: 43°C DBT
3.3 | Pipe Length : Refer Tender Layout
3.4 | Level Difference : Refer Tender Layout
3.5 | EER rating at ARI conditions
3.6 | EER rating at actual conditions
4 | OPERATING RANGE:
4.1 | Maximum rated continuous operating hours
4.2 | Cooling (Min & Max DBT)
4.3 | ODU to IDU Installation Connectivity | %
4.4 | ODU to IDU Operational Connectivity | %
5 | COMPRESSOR:
5.1 | Type 1
5.2 | Type 2
5.3 | Fixed Ref. Flow Compressor Quantity
5.4 | Fixed Ref. Flow Compressor Quantity
5.5 | Variable Ref. Flow Compressor Quantity
5.6 | Variable Ref. Flow Compressor Capacity
5.7 | Rated continuous operating hours for VRF Compressor
5.8 | Minimum idle hours required before next start of VRF compressor
6 | FAN:
6.1 | Fan Type
6.2 | Qunatity | Nos
6.3 | Fan Motor Power | kW
6.4 | Air Flow rate | CMH
7 | POWER SUPPLY:
7.1 | V/PH/Hz | V-Ph-Hz
7.2 | Minimum Circuit Amps : | Amp
7.3 | Maximum Fuse Amps : | Amp
7.4 | Maximum Starting Current : | Amp
7.5 | Total Over current Amps : | Amp
7.6 | Electrical Cable Specification
7.7 | Electrical Breaker Specification
7.8 | Communication Cable Specification
8 | REFIRGERANT & PIPING:
8.1 | Refrigerant Type / Charge (Kgs) : | Kgs
8.2 | Liquid Piping (Main Line Size) : | mm
8.3 | Suction Gas Piping (Main Line Size) : | mm
9 | UNIT DATA:
9.1 | Sound Pressure Level at 1 m : | dB(A)
Note: Please duplicate this format for more than one ODU, required for the project and provide details for all types of ODUs.